## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
1 BR-SP-B | 1 Bed Room - Special, CCU | 20 |  | 1 patient; 1-2 visitors, 1-2 staff intermittently | 24 Hours | Acoustic privacy is required | A 1 Bed Room - Special, Coronary Care will accommodate one patient for the delivery of cardiac care treatment. Glazed doors and partition walls are recommended for patient visibility and privacy. Natural light and outlook is essential; the room requires the ability to view out of the window from either the chair or bed. Acoustics: Acoustic privacy is required. Body Protected Electrical Area

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 1000 | Floor finish | 1 | Carpet also acceptable | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 1045 | Floor finish | 1 | under basin | Vinyl, non slip | Textured | Seamless, coved | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 2000 | Skirting | 1 | Feather edge vinyl skirting if carpeted | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 3060 | Wall finish | 1 | to basin | Vinyl | Prefinished | Splashback | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 3092 | Wall protection | 1 |  | MDF | Laminate | Bed protection wall panel | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 4030 | Wall protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Corner guards to 900 AFFL | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 5010 | Ceiling - Plasterboard | 1 |  | Plasterboard | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 7001 | Windows | 1 | Natural light & outlook essential. |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 7055 | Observation | 1 | with integral venetian blinds | Alum/ Glass | Powdercoat | Internal window, double glazed | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | Fabrics | 9110 | Door - 1400mm | 1 | 1400mm clear opening; latch set, observation panel optional | Solid Core | Paint | 1 1/2 leaf | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FE | FE-2800 | Basin - handwash, Type B | 1 | refer to BHWS-B (sim) |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FE | FE-36050 | Monitor - cardiac | 1 | may be telemetry |  |  |  | Yes | Yes | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FE | FE-54510 | Telephone - handset, standard | 1 |  |  |  |  | No | Yes | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FE | FE-5622 | Bed - inpatient, electric + standard patient mattress | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-12450 | Locker - bedside | 1 | mobile, 2 lockable drawers |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-1252 | Blind - Venetian integral | 1 | to internal window |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-1465 | Bracket - suction bottle | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-1480 | Bracket - ECG monitor | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-150 | Air flowmeter | 1 | Medical air |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-16200 | Table - overbed | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-16250 | Oxygen flowmeter | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-2150 | Chair - patient | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-21950 | Suction adapter | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-22000 | Suction bottle | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-2650 | Chair - visitor, patient | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-4330 | Cupboard - wardrobe | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-4600 | Curtain track - bed screen | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-4900 | Curtain track - window | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-5000 | Curtain - bed screen | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-5410 | Curtain - window, drapes | 1 | set |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FE | FF-5547 | Patient entertainment | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-5824 | Waste bin - general | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-5825 | Bracket - patient entertainment, ceiling | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-5831 | Shelf - for flowers | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-6152 | Dispenser - disposable glove | 1 | near basin |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-6156 | Dispenser - soap | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-1006 | Voice / Data outlet: double | 1 | 1 outlet for telephone |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-1090 | TV: MATV | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-11000 | Wall panel | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-1120 | Monitor connection facilities and cabling | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-6050 | Special: reading | 1 | Up/down light |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-6060 | Special: night lights | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-6200 | Light switches | 4 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-7000 | Oxygen (O2) | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-7020 | Medical Air (MA) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-7040 | Suction | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-8000 | Patient/ Staff call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-8005 | Patient call handset | 1 | call button & light switch on the handset |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-8010 | Staff/ Nurse assist call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-9000 | GPO: Single | 2 | adjacent to patient chair |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-9000 | GPO: Single | 1 | Bedhead low level, for electric bed |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-9010 | GPO: Emergency power, single (V) | 8 | Bedhead |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-9015 | GPO: Cleaner | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1 BR-SP-B | 1 Bed Room - Special, CCU | SE | S-9060 | GPO: Special: for equipment | 1 | TV (ceiling) |  |  |  | No | No | No | No | No | No | No | No | No