## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | 28 | 24 Hours |  |  | Acoustic privacy is required | A 2 Bed Room for general mental health patients; natural light and outlook is essential; The room is to be internally lockable with a master keyed lock from the outside; All fittings are to have a breaking strain of not more than 15kg. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a standard nominal thickness of 10.38mm, or equivalent approved. The 2 Bed Room - Mental Health may vary in configuration to suit different Ensuite options including: - 2 BR-MH-A Inboard Ensuite - 2 BR-MH-B Shared Ensuite with access off the corridor - 2 BR-MH-D Back to Back Ensuites Additional Design Considerations: Fittings and Furniture, removable drawers are not to be installed . If hooks are required, they must be collapsible with a breaking strain of not more than 15kg - Door & Joinery Hardware . Door hardware and joinery hardware must not provide ligature points.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FA | DWGL-025 | DOOR: 1100mm c/o, single leaf, observation panel, solid core/ safety glass, paint | 1 | Inward & outward opening; lockable; anti-ligature door hardware | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FA | DWOB-013 | OBSERVATION: through door/s, safety glass, double glazed with integral venetian blind, powdercoat | 1 | Blind control to corridor side; observation window optional | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | DWWD-002 | BLIND: holland | 1 | to external windows, curtains optional, no ligature points | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | DWWD-007 | BLIND: venetian, integral | 2 | to observation window (if provided) and door glazing | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FA | DWWH-005 | WINDOW | 1 | Essential | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | SE | ELBO-015 | SWITCH: light, single | 4 |  | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | SE | ELGP-109 | GPO: single, wall mounted | 4 | 2 per bed | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | locate in corridor outside room | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | SE | ELPR-006 | RCD: residual current device | 1 | may be located outside room - not at bedhead | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | FIBM-003 | MIRROR: fixed, acrylic | 1 | optional, may also use safety glass mirror | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | FIBM-013 | NOTICEBOARD: fixed, fabric covered | 2 | velcro compatible or artwork, optional | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | FIJO-133 | CUPBOARD: tall, single door, fixed shelves, anti ligature | 2 | anti ligature hardware | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | FIRT-035 | TRACK: curtain, window, collapsible, anti ligature | 1 | optional, if curtains installed | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FA | FLCP-003 | FLOOR FINISH: carpet, broadloom, 48 oz., 90/10 wool/nylon | 1 | Vinyl also acceptable | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FA | FLSK-007 | SKIRTING: timber, 150H, paint | 1 | Securely fixed; or floor vinyl coved skirting | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | FQBS-004 | BED: domestic, single with mattress | 2 | with no ligature points | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 2 |  | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | FQDW-025 | DESK: built in, return end, anti ligature | 2 |  | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | FQTA-001 | TABLE: bedside | 2 | heavy | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light; 1 per bed | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light, Duress call (optional) | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | SE | LIFX-001 | LIGHT: night light, tamper proof | 1 |  | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | SE | LIFX-010 | LIGHT: reading light, tamper proof | 2 | to each bed | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FFE | MMGE-019 | CHAIR: patient | 2 |  | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 |  | No | No | No | No | No | No | No | No | No
2BR-MH-A | 2 Bed Room - Mental Health, Inboard Ensuite, 28m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No