## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
ADLB | ADL Bathroom | 12 |  | 1 patient; 1 - 2 staff assisting | 24 Hours | Sound attenuation level medium, Acoustic privacy is required. | A bathroom for patient &apos;Activities of Daily Living&apos; assessment and training. The ADL Bathroom provides for training of patients to use a domestic bath, patient dressing, undressing, grooming and handwashing. Facilities include a domestic bath installed in a corner of the room, accessible toilet and handbasin and a separate shower within the room. A low height adjustable shower is required over the bath. Additional Design Requirements: - The shower area must not have a raised hob. - The entrance to the bathroom is to be flush with the adjoining corridor. Acoustics: Sound attenuation level - Medium. Acoustic privacy required. Body Protected electrical area

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
ADLB | ADL Bathroom | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | Fabrics | 2526 | Floor finish | 1 | Significant change in colour from adjacent Corridor to be avoided. Suitable for barefeet. | Vinyl | Non-slip | Seamless coved | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | Fabrics | 3070 | Wall finish | 1 | to shower area, tiles also acceptable | Vinyl | Prefinished | Wall vinyl full height | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | Fabrics | 5023 | Ceiling - Plasterboard | 1 | Water resistant flush set suspended ceiling is also acceptable | Plasterboard | Prefinished | Water resistant, drop in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | Fabrics | 8010 | Door protection | 1 |  | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | Fabrics | 8040 | Door protection | 1 | Optional. To be decided at project level | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | Fabrics | 9110 | Door - 1400mm | 1 | 1350mm clear opening, privacy latch | Solid Core | Paint | 1 1/2 leaf | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FE | FE-3201 | Bath - domestic | 1 | Warm water. |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ADLB | ADL Bathroom | FE | FE-40406 | Tapware - shower mixer | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FE | FE-47400 | Shower - hand-held | 1 | Optional. Low level over bath. |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ADLB | ADL Bathroom | FE | FE-47400 | Shower - hand-held | 1 | To shower, short lever taps. |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ADLB | ADL Bathroom | FE | FE-55605 | Toilet suite - patient | 1 |  |  |  |  | No | No | Yes | No | Yes | No | Yes | No | No
ADLB | ADL Bathroom | FE | FE-5603 | Basin - ensuite | 1 | With integral shelf for patient belongings or separate shelf. Tapware: mixer, fixture mounted. |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ADLB | ADL Bathroom | FF | FF-13700 | Mirror | 1 | above basin |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-13800 | Mirror - full length | 1 | dressing |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-19100 | Waste bin - sanitary | 1 | Optional, depends on Waste Management Policy. |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-19910 | Shelf - vanity | 1 | Or integrated with handbasin. |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-20650 | Soap / shampoo holder | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-2300 | Chair - shower | 1 | Or commode chair or combined shower/commode chair. |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-23700 | Towel rail | 1 | With grab rail fixings. |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-23865 | Transfer bench | 1 | portable - not fixed, near bath |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-3400 | Coathook | 2 | 1 @ 1000H |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-4800 | Curtain track - shower (90deg) | 1 | Optional, depends on infection control policy. |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-5300 | Curtain - shower | 1 | Optional, depends on infection control policy. |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-6156 | Dispenser - soap | 1 | To basin. Optional for shower and bath areas. |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-6160 | Dispenser - toilet paper | 1 | On hinged rail. |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-8450 | Grab rail - Shower | 1 | Combined with hand held shower. |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FF | FF-8500 | Grab rail - WC, hinged | 2 | Drop down rails both sides of WC. 1 x toilet paper dispenser, 1 x NC. |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | S-1951 | Staff assist call | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | S-4033 | Floor waste | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | S-5015 | Ventilation | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | S-5019 | Exhaust | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | S-6000 | General fluorescent | 1 | Sensor light optional |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | S-8000 | Patient/ Staff call | 3 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | S-9001 | GPO: Double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No