## Room Data
Standard Components - Room Data Sheet
Date of issue: 26.04.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ADLL | ADL Laundry | 8 | up to 24 Hours | 1 patient, 1 staff |  |  | The ADL Laundry provides domestic facilities for the training and assessment of patients in Activities of Daily Living (ADL) tasks. The room will include a domestic washing machine and dryer which, if front loading models are selected, may be placed on plinths to raise machines to an accessible height to support common ADL training and assessment tasks as per service requirements. A laundry tub and storage for ironing equipment are also provided. Additional Considerations: An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. If multiple ADL rooms are combined into an ADL suite nurse call buttons can be rationalised into a central location. The space may be provided as an open bay that is collocated with other ADL rooms. If open, the impact of noise on adjacent areas must be considered.

## Items
Standard Components - Items in room
Date of issue: 26.04.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
ADLL | ADL Laundry | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
ADLL | ADL Laundry | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
ADLL | ADL Laundry | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
ADLL | ADL Laundry | FA | WLWA-007 | WALL FINISH: splashback | 1
ADLL | ADL Laundry | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
ADLL | ADL Laundry | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | plasterboard flush set ceiling is also acceptable
ADLL | ADL Laundry | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
ADLL | ADL Laundry | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
ADLL | ADL Laundry | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ADLL | ADL Laundry | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 2
ADLL | ADL Laundry | FFE | FIJO-156 | CUPBOARD: wall mount, single door, adj shelves | 1
ADLL | ADL Laundry | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ADLL | ADL Laundry | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to sink
ADLL | ADL Laundry | FFE | FIDI-030 | DISPENSER: soap | 1 | to sink
ADLL | ADL Laundry | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
ADLL | ADL Laundry | FFE | FQSM-030 | TROLLEY: laundry, basket | 1 | optional
ADLL | ADL Laundry | FFE | FQGE-015 | DRYER: clothes, domestic | 1
ADLL | ADL Laundry | FFE | FQGE-028 | IRON: clothes, electric | 1
ADLL | ADL Laundry | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
ADLL | ADL Laundry | FFE | HYBA-064 | SINK: single, laundry | 1 | with overflow drain, warm water
ADLL | ADL Laundry | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 | with inset laundry tub
ADLL | ADL Laundry | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead also acceptable
ADLL | ADL Laundry | FFE | MMAH-039 | PLINTH: laundry | 2
ADLL | ADL Laundry | FFE | FIJO-222 | CUPBOARD: tall, single door, fixed shelf, ADL Laundry | 1
ADLL | ADL Laundry | FFE | FQCW-063 | MACHINE: washing, domestic, front loading | 1
ADLL | ADL Laundry | SE | ELPR-006 | RCD: residual current device | 1 | type 1 10mA in accordance with AS/NZS 3003
ADLL | ADL Laundry | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLL | ADL Laundry | SE | HYTP-008 | OUTLET: cold water | 1 | to washing machine
ADLL | ADL Laundry | SE | HYDR-004 | DRAIN: floor waste | 1
ADLL | ADL Laundry | SE | ELBO-015 | SWITCH: light, single | 1
ADLL | ADL Laundry | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLL | ADL Laundry | SE | ELGP-109 | GPO: single, wall mounted | 2 | to washing machine and dryer
ADLL | ADL Laundry | SE | ELGP-208 | GPO: double, wall mounted | 1 | 30mA RCD protection