## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
AHBBF | After Hours Blood Fridge | 3 |  | 1 - 2 intermittently | 24 Hours |  | The After Hours Blood Fridge is a discreet area for refrigerated storage of blood and blood products for after hours access by authorised personnel. The After Hours Blood Fridge may be located in close proximity to a Critical Care Unit.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
AHBBF | After Hours Blood Fridge | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | Fabrics | 4030 | Wall protection | 1 | As required; Equal to' Acrovyn' | Composite | Prefinished PVC | Corner guards to 900 AFFL | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | Fabrics | 5010 | Ceiling - Plasterboard | 1 |  | Plasterboard | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | FE | FE-21805 | Freezer - blood products | 1 | with temperature alarm, optional |  |  |  | Yes | Yes | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | FE | FE-44300 | Refrigerator - blood products | 1 | with temperature alarm |  |  |  | Yes | Yes | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | FF | FF-1050 | Bench - laminate | 1 | for recording |  |  |  | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | FF | FF-17385 | Pinboard/ whiteboard combination | 1 | combination unit |  |  |  | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | SE | S-1005 | Voice / Data outlet: single | 2 | 1 to each blood fridge / freezer |  |  |  | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | SE | S-1085 | Temperature monitor & alarm | 2 | 1 to each blood fridge/ freezer |  |  |  | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | SE | S-9010 | GPO: Emergency power, single (V) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
AHBBF | After Hours Blood Fridge | SE | S-9010 | GPO: Emergency power, single (H) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No