## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ANIN | Anaesthetic Induction Room | 15 | Available 24 Hours | 1 patient; up to 3 staff |  | Acoustic privacy is required | The Anaesthetic Room is for holding patients on mobile beds or trolleys prior to operative procedures at times when the Operating Room is not available. Local, regional or general anaesthesia may be administered in this area. Depending on special circumstances an Anaesthetic Induction Room of 18 m2 is also acceptable.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ANIN | Anaesthetic Induction Room | FA | CLCN-007 | CORNICE: plasterboard, flush coved between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FA | DWGL-042 | DOOR: 1500mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | sliding covers to obs panels | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ELBO-015 | SWITCH: light, single | 2 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ELGP-105 | GPO: single, on services panel | 2 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ELGP-106 | GPO: single, special, for equipment | 2 | clock, procedure light | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ELGP-109 | GPO: single, wall mounted | 3 | to walls (1 for fridge) | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to monitor | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 4 | to bench | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ELGP-206 | GPO: double, on services panel, RCD protected | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIDI-021 | DISPENSER: mask | 1 | to entry | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIHR-001 | BRACKET: arm, cable/hose support, wall mounted | 1 | optional | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIHR-011 | BRACKET: for monitor | 1 | optional | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | on equipment rail | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 3 | 457mmx457mm, over bench | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 | open under part | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIJO-102 | CUPBOARD: drawer unit | 1 | under bench | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 2 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIJO-148 | CUPBOARD: wall mount, double door, glazed, adj shelves, lockable | 3 | overbench | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FIRT-012 | RAIL: equipment | 1 | under services panel | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FA | FLVY-006 | FLOOR FINISH: vinyl, seamless, coved, non slip, textured | 1 | under basin | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FQCW-004 | BIN: waste, clinical, 120L | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 | on bench | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FQSM-016 | TROLLEY | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 10 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1 | Refer to BWHS-A (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
ANIN | Anaesthetic Induction Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ITCL-005 | BUTTON: nurse call, orderly / porter | 1 | optional | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | ITCL-016 | CLOCK: clock system slave, analogue | 1 |  | Yes | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 outlet for telephone | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | to bench | No | Yes | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | LIFX-008 | LIGHT: task light, built in | 2 | under O/H cupboards | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1 |  | Yes | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | MGFP-002 | FLOWMETER: medical air | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | MGFP-004 | FLOWMETER: oxygen | 2 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | MMGE-002 | ADAPTER: suction | 2 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | MMGE-036 | FRIDGE: drugs, underbench | 1 | under bench, optional | Yes | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | MMGE-100 | SUCTION BOTTLE | 2 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FFE | MMHA-008 | MONITOR: patient, cardiac with vital signs | 1 | optional | Yes | Yes | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | recessed | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FA | WLPR-019 | WALL PROTECTION: crash rail, at 900 AFFL, prefinished PVC | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
ANIN | Anaesthetic Induction Room | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin, tiles also acceptable | No | No | No | No | No | No | No | No | No