## Room Data
Standard Components - Room Data Sheet
Date of issue: 24.06.2022
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
BPTS | Bay - Pneumatic Tube Station | 1 | Available 24 Hours | accessed by staff intermittently |  |  | The Bay - Pneumatic Tube Station (PTS) provides an area for dispatching and receiving of items via the pneumatic tube system. This Standard Component represents a department based bay and additional area, FFE and services will be required for a central receiving and processing area in a pathology or pharmacy department. Additional Considerations: To be collocated or located with clear oversite from a staff station or within a staff only area. Arrival notification alarms must be programmable for different times and scenarios depending on service requirements. Security requirements are to be considered. If the station is to receive deliveries from Pharmacy or is in an area accessed by the public then secure access to a lockable receiving basket may be required depending on location of the bay. Station may be a pass through or end station and receive/dispatch through the floor or ceiling depending on location and system configuration. Radio frequency identification (RFID) technology may be considered by projects to reduce errors, improve traceability and to enable dynamic/intuitive routing to reduce "traffic jams". This technology involves embedded RFID tags in cannisters that are read by receivers at tube stations on dispatch/arrival and at interchange points in the system. Where multiple services send/receive products via the pneumatic tube system, e.g. pathology and pharmacy, colour coding the cannisters for the different streams is recommended. Colour coding to differentiate between cannisters from high priority areas, e.g. emergency and intensive care vs general wards may also be considered.

## Items
Standard Components - Items in room
Date of issue: 24.06.2022
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
BPTS | Bay - Pneumatic Tube Station | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 4 | coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | coordinated with adjacent wall protection
BPTS | Bay - Pneumatic Tube Station | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BPTS | Bay - Pneumatic Tube Station | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 | coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | FFE | FQSN-001 | BASKET: drop in, pneumatic station | 1 | may be lockable depending on location, service and security requirements
BPTS | Bay - Pneumatic Tube Station | FFE | MMLA-072 | RACK: canister storage (pneumatic tube) | 1 | quantity to suit service requirements
BPTS | Bay - Pneumatic Tube Station | FFE | MMGE-097 | STATION: pneumatic tube | 1 | with audible alarm
BPTS | Bay - Pneumatic Tube Station | SE | LIFX-015 | LIGHT: pneumatic tube alert light | 1
BPTS | Bay - Pneumatic Tube Station | SE | ELGE-001 | DIRECT CONNECTION: power | 1 | direct connection to station