## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
CHST-20 | Change - Staff (Male/Female), 20m2 | 20 | 24 Hours | Up to 5 |  | Sound attenuation level medium, Acoustic privacy is required. | Staff Change areas are provided for staff that are required to change into appropriate work clothing or gowns, to store their street clothing and to perform personal ablutions. Change rooms should be divided into male and female areas on a proportional basis and will include showers, toilets and handbasins. Secure storage for personal property should be provided. Secured, staff only access to Change Rooms is required. The area may increase according to the number of staff showers/toilets and lockers to be accommodated. Allow an additional 2m2 for each additional toilet and shower, 1m2 for each additional basin and 0.5m2 for each additional locker.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
CHST-20 | Change - Staff (Male/Female), 20m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | Secure staff only access | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | above basin | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIBM-007 | MIRROR: fixed, glass, full length | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | 1 per basin. | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 2 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 | to shower cubicle | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIGE-003 | BENCH SEAT: fixed, indoor | 1 | to shower cubicle | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIHR-026 | HOOK: coat | 3 | 1 per cubicle. | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIJO-191 | SHELF: above basin | 1 | Or integrated with basin. | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIRT-013 | RAIL: hanging, utility | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FIRT-033 | TRACK: curtain, shower | 1 | optional | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | Default = coved vinyl: or tiled skirting to tiled floor | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | Default = vinyl: tiles also acceptable | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | Suitable for barefeet. To shower, default = vinyl, tiles also acceptable. | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FQCW-037 | BIN: waste, sanitary | 2 | To Female Change Rooms. Optional, depends on Waste Management Policy. | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1 | Optional | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FQGE-011 | CURTAIN: shower | 1 | Optional, depends on Infection Control Policy | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FQSN-014 | CABINET: coat/shoes valet | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | FQSN-048 | LOCKER: 2 tier (half size) | 8 | 16 half lockers | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | HYBA-011 | BASIN: handwash, Type C | 2 | With vanity, or ensuite basin with integral shelf for staff belongings. | No | No | Yes | No | Yes | Yes | Yes | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | SE | HYDR-004 | DRAIN: floor waste | 2 |  | No | No | No | No | No | No | Yes | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | HYTP-018 | SHOWER: fixed rose | 1 | with adjustable shower head | No | No | Yes | No | Yes | Yes | Yes | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 2 |  | No | No | Yes | No | Yes | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | HYWC-008 | TOILET SUITE: standard | 2 |  | No | No | Yes | No | No | Yes | Yes | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | Wall telephone. | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1 |  | No | Yes | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | SE | ITSE-038 | READER: access control, general | 1 | or keypad, on entry door from corridor | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | MMGE-110 | TROLLEY: clean linen, small | 1 | Number to suit service. | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | WLPT-004 | PARTITION: shower | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FFE | WLPT-005 | PARTITION: toilet | 2 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FA | WLWA-007 | WALL FINISH: splashback | 1 | Selection of material to comply with Part D Infection Prevention and Control AusHFG. | No | No | No | No | No | No | No | No | No
CHST-20 | Change - Staff (Male/Female), 20m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 |  | No | No | No | No | No | No | No | No | No