## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Briefing
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics | Description / Special Requirements
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
CLUR-14 | Clean Utility, 14m2 | 14 |  | 1 - 2 staff | 24 Hours |  | A room for the storage and preparation of clean and sterile consumables and equipment for patient treatment; secure storage and preparation of medications, including intravenous fluids. It may also function as an alternative storage area for the medication trolley. The room may provide storage for drugs of dependence in accordance with relevant legislation. The Clean Utility 14m2 will provided access doors from both sides of the room. Secure staff only access to the room will be required. Refer to project specific requirements for automated medication management systems. Storage provisions to meet service / functionality design and OH&S demands. This includes (and not limited to) proprietary storage systems.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
CLUR-14 | Clean Utility, 14m2 | FE | FE-11400 | Computer - PC & monitor | 0 | Or mobile device as per hospitals ICT strategy |  |  |  | Yes | Yes | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FE | FE-2800 | Basin - handwash, Type B | 1 | refer to BHWS-B (sim). Elbow action levers or handsfree optional. |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
CLUR-14 | Clean Utility, 14m2 | FE | FE-44360 | Refrigerator - drugs, small | 1 | Or large drug fridge, size depends on operational policy and functional requirement. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FE | FE-49111 | Sink - 450x350x250D | 0 | Default = no sink, optional |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
CLUR-14 | Clean Utility, 14m2 | FE | FE-49111 | Sink - 450x350x250D | 1 |  |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
CLUR-14 | Clean Utility, 14m2 | FE | FE-54510 | Telephone - handset, standard | 1 | Wall or bench mounted, optional. |  |  |  | No | Yes | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FE | FF-5559 | Automated medication management device | 1 | Optional, fixed or mobile solution depending on local medication management systems. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FE | FE-41150 | Printer - labels | 0 | for medication |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FE | FE-4045 | Tapware - elbow mixer | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-1050 | Bench - laminate | 2 | Length and number to suit, refer RLS or project specific requirements. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-12900 | Wire panel - for storage-bins | 2 | Above bench, optional. Depends on functionality, infection control and cleaning policies. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-1470 | Bracket - sharps | 1 | Wall mounted or trolley. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-17312 | Pharmacy bin; returns | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-19062 | Safe - dangerous drugs, medium | 1 | Or large drug safe, size depends on operational policy and functional requirement. Reinforce wall fixings to suit weight capacity. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-19700 | Sharps bin | 1 | Wall mounted or trolley. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-20015 | Shelving unit - PPE | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-4410 | Cupboard - under bench | 2 | Optional, with adjustable shelves. Number and type to suit design and functionality. Refer RLS or project specific requirements. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-4480 | Cupboard - wall mounted, glass doors | 0 | Optional, over bench, lockable, adjustable shelves. Number and type to suit design and functionality. Refer RLS or project specific requirements. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to hand basin |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-6156 | Dispenser - soap | 1 | to hand basin |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to hand basin |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-6600 | Trolley - dressing | 1 | Number to suit service. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-6153 | Dispenser - moisturiser | 1 | Optional |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-5830 | Dispenser - antiseptic hand rub | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-5933 | Cabinet - wall mounted, above bench | 0 | Number and type of storage to suit design and functionality. Refer RLS or project specific requirements. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-2965 | Shelf - under bench | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-5598 | Shelving unit - adjustable, full height | 1 | IV fluid, etc. Number and type to suit design and functionality. Refer RLS or project specific requirements. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-5597 | Shelving unit - over bench, adjustable | 1 | Optional. Number and type to suit design and functionality. Refer RLS or project specific requirements. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-5931 | Shelving unit - over bench | 2 | Optional. Number and type to suit design and functionality. Refer RLS or project specific requirements. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-5580 | Storage bins - stainless steel wire mesh | 2 | For louvred panels, optional. Depends on functionality, infection control and cleaning policies. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | FF | FF-13600 | Trolley - medication | 1 | Number to suit service |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-9000 | GPO: Single | 4 | 2 above bench |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-9010 | GPO: Emergency power, single (V) | 1 | For drug refrigerator. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-9011 | GPO: Emergency power, double (H) | 2 | Include only if automated medication management system used. Refer manufacturer's specifications. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-1005 | Voice / Data outlet: single | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-1006 | Voice / Data outlet: double | 1 | 1 outlet for telephone |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-1006 | Voice / Data outlet: double | 1 | Include only if automated medication management system used. Refer manufacturer's specifications. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-6200 | Light switches (2-way) | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-6200 | Light switches (pelmet) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-6055 | Special: task light, built in | 2 | Optional, under O/H cupboards |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-8040 | Annunciator | 1 | to be heard in this room |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | SE | S-10020 | Card access | 2 | Secure staff access, depends on medication storage provisions. |  |  |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 2526 | Floor finish | 1 | Significant change in colour to be avoided. | Vinyl | Non-slip | Seamless coved | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 3052 | Wall finish | 1 |  | Vinyl | Prefinished | Wall vinyl to 1500 AFFL | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 5007 | Ceiling - Plasterboard | 1 | Laminate infill also acceptable. Between above bench joinery and ceiling. | Plasterboard | Paint | Bulkhead | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 5010 | Ceiling - Plasterboard | 1 | for security reasons | Plasterboard | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 9004 | Door - 1100mm | 1 | 910mm clear opening, lockable | Solid Core/ Glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 2530 | Door protection | 1 |  | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 2529 | Door protection | 1 |  | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
CLUR-14 | Clean Utility, 14m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No