## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
COMM | Communications Room | 12 |  | 1 - 2 intermittently | 24 Hours |  | A secure room for engineering services to accommodate communications racks, interface control panels for communication systems which may include MATV, Nurse Call and Fire/EWIS system and voice/ data backbone cabling. Equipment located in this room may require uninterruptible power. Area shown is indicative only. The size of the Communications Room will be project specific and will vary according to engineering consultant advice.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
COMM | Communications Room | Fabrics | 1030 | Floor finish | 1 |  | Vinyl | Anti-static | Seamless, coved | bar: Connections Ele to Connections Stm
COMM | Communications Room | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | bar: Connections Ele to Connections Stm
COMM | Communications Room | Fabrics | 2713 | Door protection | 1 |  |  |  | Kick plate 300 AFFL | bar: Connections Ele to Connections Stm
COMM | Communications Room | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable | bar: Connections Ele to Connections Stm
COMM | Communications Room | Fabrics | 5030 | Ceiling - Plasterboard | 1 |  | Plasterboard | Prefinished | Drop-in tiles, 600x1200 | bar: Connections Ele to Connections Stm
COMM | Communications Room | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | bar: Connections Ele to Connections Stm
COMM | Communications Room | Fabrics | 8040 | Door protection | 1 | Optional. To be decided at project level. | Composite | Prefinished PVC | To door frame | bar: Connections Ele to Connections Stm
COMM | Communications Room | Fabrics | 9004 | Door - 1100mm | 1 | Lockable. | Solid Core/ Glass | Paint | Single leaf, observation panel | bar: Connections Ele to Connections Stm
COMM | Communications Room | FE | FE-10655 | Communications board | 1 | As required. Refer project specific requirements. |  |  |  | Yes | No | No | No | No | No | No | No | No
COMM | Communications Room | FE | FE-10890 | Rack - communications | 1 | As required. Refer project specific requirements. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
COMM | Communications Room | FE | FE-10895 | Rack - voice, IDF | 1 | Optional. Refer project specific requirements. |  |  |  | Yes | No | No | No | No | No | No | No | No
COMM | Communications Room | FE | FE-11200 | Computer - mainframe | 1 | As required. Refer project specific requirements.. | bar: Connections Ele to Connections Stm
COMM | Communications Room | FE | FE-11400 | Computer - PC & monitor | 2 | Flat screen, as required. Refer project specific requirements. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
COMM | Communications Room | FE | FE-11900 | Computer - server | 1 | As required. Refer project specific requirements. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
COMM | Communications Room | FE | FE-17100 | Distribution Board | 1 | UPS, single phase |  |  |  | Yes | No | No | No | No | No | No | No | No
COMM | Communications Room | FE | FE-54510 | Telephone - handset, standard | 1 |  |  |  |  | No | Yes | No | No | No | No | No | No | No
COMM | Communications Room | FE | FE-8760 | Control panel - fire & EWIS | 1 | optional |  |  |  | Yes | No | No | No | No | No | No | No | No
COMM | Communications Room | FF | FF-1050 | Bench - laminate | 1 | Optional, length to suit layout, refer RLS or project specific requirements. | bar: Connections Ele to Connections Stm
COMM | Communications Room | FF | FF-2100 | Chair - ergonomic, office | 1 | optional | bar: Connections Ele to Connections Stm
COMM | Communications Room | FF | FF-24405 | Whiteboard - magnetic | 1 | optional | bar: Connections Ele to Connections Stm
COMM | Communications Room | SE | S-10000 | Motion detector / alarm | 1 | bar: Connections Ele to Connections Stm
COMM | Communications Room | SE | S-10020 | Card access | 1 | bar: Connections Ele to Connections Stm
COMM | Communications Room | SE | S-1006 | Voice / Data outlet: double | 3 | Number depends on equipment. Refer project specific requirements. | bar: Connections Ele to Connections Stm
COMM | Communications Room | SE | S-2088 | Light switch: single | 1 | bar: Connections Ele to Connections Stm
COMM | Communications Room | SE | S-3040 | EWIS | 1 | Optional. |  |  |  | Yes | No | No | No | No | No | No | No | No
COMM | Communications Room | SE | S-5000 | Airconditioning | 1 | Temperature alarm for heat-generating equipment. | bar: Connections Ele to Connections Stm
COMM | Communications Room | SE | S-6000 | General fluorescent | 1 | Sensor light optional | bar: Connections Ele to Connections Stm
COMM | Communications Room | SE | S-9001 | GPO: Double | 10 | As required. Refer project specific requirements. | bar: Connections Ele to Connections Stm
COMM | Communications Room | SE | S-9020 | UPS (uninterruptible power) | 1 | as required | bar: Connections Ele to Connections Stm
COMM | Communications Room | SE | S-9060 | GPO: Special: for equipment | 4 | As required. Refer project specific requirements. | bar: Connections Ele to Connections Stm