## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Briefing
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics | Description / Special Requirements
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | 12 | For bariatric consult requirements refer to Treatment Room options | 1 patient: 1-2 staff, 1-2 visitors | 24 Hours | Sound attenuation level high, Acoustic privacy is required. | The Consult Room ENT/ Ophthalmology will provide for private consultation and examination of patients for ENT/ Ophthalmology using specialised equipment. The Consult room may also be used for general consultations. A second egress door may be required for staff safety and security and/or staff access. A distance of 3m is required between the eye chart and mirror for effective use. Requires dimmable lighting. Acoustics: Sound attenuation level - high; Acoustic privacy essential. Body Protected electrical area

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-11400 | Computer - PC & monitor | 1 | To desk, high resolution for PACS viewing |  |  |  | Yes | Yes | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-15900 | Diagnostic set - wall mounted | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-20350 | Examination couch - electric | 1 | Hi/Low operation |  |  |  | Yes | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-2800 | Basin - handwash, Type B | 1 | Tapware; elbow action levers or handsfree optional |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-31701 | Light - examination, wall mount | 1 | wall mounted or ceiling mounted, optional |  |  |  | Yes | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-36915 | Light box - eye chart | 1 | Consider use of a wall monitor for viewing eye charts as an alternative and where used include bracket, power and data as needed. |  |  |  | Yes | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-41100 | Printer - networked | 0 | EMR/E-med compatible. Optional printing strategy (centralised vs. decentralised) to be decided at project level. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-44360 | Refrigerator - drugs, small | 1 | eye medications |  |  |  | Yes | Yes | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-50600 | Slit lamp | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-54520 | Telephone - handset, handsfree | 1 | to desk |  |  |  | No | Yes | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FE | FE-5836 | Xray viewer - 2 screen, portable | 0 | 1 per department, number and location to be determined at project level |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-13725 | Mirror - hinged | 1 | wall mounted, for eye chart |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-1465 | Bracket - suction bottle | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-1470 | Bracket - sharps | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-150 | Air flowmeter | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-16250 | Oxygen flowmeter | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-17360 | Pinboard - fabric covered | 1 | Over desk, optional |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-19700 | Sharps bin | 1 | Wall mounted |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-20000 | Shelving unit - adjustable | 1 | Over desk, number to suit |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-2100 | Chair - ergonomic, office | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-21950 | Suction adapter | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-22000 | Suction bottle | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-2600 | Chair - visitor, office | 2 | Consider weight capacity of chair |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-3400 | Coathook | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-4600 | Curtain track - bed screen | 1 | to exam couch |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-5000 | Curtain - bed screen | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-5900 | Desk | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to hand basin |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-6156 | Dispenser - soap | 1 | to hand basin |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to hand basin |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-6153 | Dispenser - moisturiser | 1 | Depends on operational policy |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-5830 | Dispenser - antiseptic hand rub | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-5824 | Waste bin - general | 2 | To hand basin |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-21020 | Sphygmomanometer - portable | 1 | 1 per 6 consult rooms, ratio to be determined at project level |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-775 | Dispenser - bed roll | 1 | Or provided as an attachment to exam couch |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FF | FF-7100 | Trolley - ENT | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-9000 | GPO: Single | 1 | low level for electric exam couch, optional |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-9000 | GPO: Single | 3 | Diagnostic set, light box, slit lamp |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-9000 | GPO: Single | 1 | for BYO devices at desk |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-9000 | GPO: Single | 1 | for exam light |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-9010 | GPO: Emergency power, single (V) | 1 | Refrigerator, if refrigerator required |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-9001 | GPO: Double | 1 | patient examination area |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-9001 | GPO: Double | 2 | workstation / desk area |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-9011 | GPO: Emergency power, double (H) | 1 | patient examination area |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-1005 | Voice / Data outlet: single | 1 | For refrigerator, if refrigerator required |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-1006 | Voice / Data outlet: double | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-1085 | Temperature monitor & alarm | 1 | Refrigerator if required |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-8000 | Patient/ Staff call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-8005 | Patient call handset | 1 | as required |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-10005 | Duress alarm | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-7000 | Oxygen (O2) | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-7020 | Medical Air (MA) | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-7040 | Suction | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | S-11000 | Wall panel | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 1000 | Floor finish | 1 | Default = vinyl: Carpet also acceptable | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 1020 | Floor finish | 1 | Under basin, significant change in colour to be avoided. | Vinyl, non-slip | Safety | Seamless, coved | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 2906 | Wall finish | 1 | Selection of material to comply with Part D Infection Prevention & Control AusHFG. |  |  | Splashback behind basin | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 5007 | Ceiling - Plasterboard | 1 | Between above bench joinery and ceiling, default joinery | Plasterboard | Paint | Bulkhead | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 5060 | Ceiling - Acoustic | 1 |  | Acoustic | Prefinished | Drop-in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 9125 | Door - 1400mm | 1 | 910/1400mm clear opening or a 1200mm clear opening single door. Bariatric provision to be decided at project level. | Solid Core/ Glass | Paint | 1 1/2 leaf, observation panel | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 2529 | Door protection | 2 |  | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 2712 | Door protection | 2 |  |  |  | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | Fabrics | 2000 | Skirting | 5 | Default = coved skirting: or vinyl featheredge skirting over carpet | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No