## Room Data
Standard Components - Room Data Sheet
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
CONS | Consult Room | 12 | 24 Hours | 1 patient: 1-2 staff, 1-2 visitors |  | Sound attenuation level high, Acoustic privacy is essential. | The Consult Room will provide for private consultation and physical examination of patients with or without support persons present. A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements.

## Items
Standard Components - Items in room
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
CONS | Consult Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CONS | Consult Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
CONS | Consult Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
CONS | Consult Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
CONS | Consult Room | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
CONS | Consult Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CONS | Consult Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 2 | to exam couch
CONS | Consult Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
CONS | Consult Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | 1 1/2 leaf door is also acceptable as required
CONS | Consult Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 1 | to patient/visitor chairs
CONS | Consult Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CONS | Consult Room | FA | DWGL-077 | DOOR: 850mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | optional, second door for egress
CONS | Consult Room | FFE | MGFP-002 | FLOWMETER: medical air | 1 | optional, provide if medical air required
CONS | Consult Room | FFE | FIDI-003 | DISPENSER: bedroll | 1 | may be provided as an attachment to exam couch
CONS | Consult Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1 | optional, provide if suction required
CONS | Consult Room | FFE | FIHR-016 | BRACKET: for sharps bin | 1
CONS | Consult Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
CONS | Consult Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CONS | Consult Room | FFE | FIHR-026 | HOOK: coat | 2
CONS | Consult Room | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
CONS | Consult Room | FFE | FQGE-010 | CURTAIN: privacy screen | 1
CONS | Consult Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CONS | Consult Room | FFE | MMGE-030 | DIAGNOSTIC SET: portable | 1 | may be wall mounted/mobile on stand
CONS | Consult Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
CONS | Consult Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CONS | Consult Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CONS | Consult Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
CONS | Consult Room | FFE | FIBM-006 | MIRROR: fixed, glass | 1
CONS | Consult Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1 | optional, provide if oxygen required
CONS | Consult Room | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
CONS | Consult Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
CONS | Consult Room | FFE | MMGE-002 | ADAPTER: suction | 1 | optional, provide if suction required
CONS | Consult Room | FFE | MMGE-100 | SUCTION BOTTLE | 1 | optional, provide if suction required
CONS | Consult Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
CONS | Consult Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
CONS | Consult Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
CONS | Consult Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | high resolution monitor for PACS viewing
CONS | Consult Room | FFE | MMBE-023 | COUCH: examination, electric, mobile | 1 | hi/low operation
CONS | Consult Room | FFE | LIFX-026 | LIGHT: examination, wall mounted | 1 | may be ceiling mounted
CONS | Consult Room | FFE | ITNE-023 | PRINTER: networked | 1 | optional
CONS | Consult Room | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1
CONS | Consult Room | FFE | FQDW-037 | DESK: adj height, 1500W x 750D x 750H nom. | 1
CONS | Consult Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
CONS | Consult Room | FFE | FQBS-058 | CHAIR: visitor, patient, with arms | 3 | consider weight capacity of chairs
CONS | Consult Room | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | to desk
CONS | Consult Room | SE | ELPR-006 | RCD: residual current device | 3
CONS | Consult Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
CONS | Consult Room | SE | ELBO-015 | SWITCH: light, single | 2 | 1 to exam light
CONS | Consult Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | optional
CONS | Consult Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | optional
CONS | Consult Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | optional
CONS | Consult Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1
CONS | Consult Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
CONS | Consult Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level, for electric couch
CONS | Consult Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | for exam light
CONS | Consult Room | SE | ELGP-208 | GPO: double, wall mounted | 3 | 2x below desk, 1x above desk
CONS | Consult Room | SE | ITSE-006 | BUTTON: duress, fixed | 1 | in discreet location easily accessible by staff
CONS | Consult Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
CONS | Consult Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
CONS | Consult Room | SE | ELGP-205 | GPO: double, on services panel | 1
CONS | Consult Room | SE | ELGP-222.1 | GPO: emergency power, double, on services panel (V) | 1