## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.06.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
CORR | Corridor - Patient Treatment Areas | 0 | 24 hours |  |  |  | The Corridor - Patient Treatment Areas indicates requirements for circulation spaces between patient treatment spaces, patient accommodation and clinical support spaces within departments. Corridor widths will vary between departments and will depend on the requirement for frequent bed transportation; widths must allow for the safe movement and passing of trolleys, beds, wheelchairs and other mobile equipment as required. Provision should be made for situations where oversized additional equipment, e.g. bed extensions or bariatric beds, are in use. Guidance for the calculation of areas (m2) for corridors is provided for in Health Planning Unit Schedules of Accommodation as circulation percentages. Refer to AusHFG Part C: Design for Access, Mobility, Safety and Security for further information. Additional Design Considerations: Wall protection is recommended to protect wall linings and finishes from damage from impact. The height of the wall protection will be dependent on equipment frequently moved through the space; a height range of 900mm minimum up to 1500mm is recommended depending on service requirements. Handrails are to be provided along not less than one side of all corridors in patient care areas to provide assistance and support for patients and visitors. Handrails are to be continuous along the corridors wherever practical. Cleaner's electrical outlets to be provided at regular intervals as per mandatory requirements. Corridor lighting, where patients are transported on beds/trolleys, should be positioned to prevent unnecessary glare to patient eyes. Light fittings shall be recessed, flush fitting and sealed to prevent dust ingress. Manual controls to power-operated doors shall be located on the continuous accessible path of travel no closer than 500 mm from an internal corner and between 1000 mm to 2000 mm from the hinged door leaf in any position as per the requirements of AS1428.1.

## Items
Standard Components - Items in room
Date of issue: 28.06.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
CORR | Corridor - Patient Treatment Areas | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CORR | Corridor - Patient Treatment Areas | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 16
CORR | Corridor - Patient Treatment Areas | FA | WLPR-006 | WALL PROTECTION: corner guards | 6 | coordinated with adjacent wall protection
CORR | Corridor - Patient Treatment Areas | FA | FIRT-010 | HANDRAIL | 4 | provided to at least one side of the corridor, to be continuous wherever practical; may be combined with crash rail if provided
CORR | Corridor - Patient Treatment Areas | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
CORR | Corridor - Patient Treatment Areas | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
CORR | Corridor - Patient Treatment Areas | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CORR | Corridor - Patient Treatment Areas | FA | WLPR-026 | WALL PROTECTION: rigid wall sheeting | 12 | height dependent on service requirements, crash rails are also acceptable
CORR | Corridor - Patient Treatment Areas | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 | quantity to suit layout and infection control policies
CORR | Corridor - Patient Treatment Areas | SE | ITCL-001 | ANNUNCIATOR: nurse call | 1 | ceiling mounted; quantity to suit layout and service requirements
CORR | Corridor - Patient Treatment Areas | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | quantity and location to comply with mandatory requirements.