## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
DENSR-16 | Dental Surgery, 16m2 | 16 |  | 1 patient, 1-2 staff; 1 support person as required | Available 24 Hours | Sound attenuation level high, Acoustic privacy is required. | The Dental Surgery provides for dental consultation, examination and treatment for patients. An external outlook is desirable. The 16m2 room provides for access by patient trolleys as required. Acoustics: sound attenuation level high; Acoustic privacy is required Body Protected electrical area Additional Design Considerations: - Radiation shielding to be advised by Radiation Consultant - Services will be required for the dental chair unit which will be dependant on the chair model and supplier and will include dental air, dental suction, filtered water, power and drainage.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
DENSR-16 | Dental Surgery, 16m2 | FE | FE-11400 | Computer - PC & monitor | 1 | flat screen |  |  |  | Yes | Yes | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FE | FE-15650 | Dental - chair, electric | 1 |  |  |  |  | Yes | No | Yes | No | No | No | Yes | No | No
DENSR-16 | Dental Surgery, 16m2 | FE | FE-15800 | Dental - X-ray unit, wall mount | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FE | FE-3120 | Basin - vanity | 1 |  |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
DENSR-16 | Dental Surgery, 16m2 | FE | FE-31605 | Light - dental | 1 | part of chair service unit |  |  |  | Yes | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FE | FE-47800 | Sink, SS - single in bench | 1 | warm water |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
DENSR-16 | Dental Surgery, 16m2 | FE | FE-54510 | Telephone - handset, standard | 1 | to bench |  |  |  | No | Yes | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FE | FE-68600 | Xray viewer - 1 screen | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FE | FE-9000 | Dental - chair service unit (spitoon) | 1 | includes intrument tray, light & spitoon; spitoon is optional, depending on operational policy |  |  |  | Yes | No | Yes | No | No | No | Yes | No | No
DENSR-16 | Dental Surgery, 16m2 | FE | FE-4045 | Tapware - elbow mixer | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FE | FF-16955 | Lifter - patient, ceiling mounted | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-1050 | Bench - laminate | 1 | with inset basin & sink, to 2 sides, open uner part for workstation and underbench mobile units |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-11200 | IV track - ceiling mounted | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-1250 | Blind - Venetian | 1 | to external windows, if provided |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-1465 | Bracket - suction bottle | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-1470 | Bracket - sharps | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-16250 | Oxygen flowmeter | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-19700 | Sharps bin | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-21680 | Stool - adjustable, mobile | 2 | 1 high ergonomic stool for 900H workstation bench |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-21950 | Suction adapter | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-22000 | Suction bottle | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-23930 | Trolley - dentist's | 1 | under bench; dental instruments and supplies |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-24400 | Whiteboard | 1 | 500x500 (optional) |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-2655 | Chair - visitor | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-3350 | Clock - battery operated | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-4410 | Cupboard - under bench | 2 | under work bench; adjustable shelves |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-4430 | Cupboard - drawer unit | 1 | under bench, with slide out tray |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-4470 | Cupboard - wall mounted, lockable | 2 | over bench, with adjustable shelves |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to vanity basin |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-6156 | Dispenser - soap | 1 | to vanity basin |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to vanity basin |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-6163 | Dispenser - mask | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-9100 | Hook - heavy duty | 2 | for lead aprons; may also use wall mounted hanging rail |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-44711 | Overbench single door lockable (600hx400wx350d) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-44716 | Overbench double door lockable (600hx800wx350d) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FF | FF-5824 | Waste bin - general | 1 | under bench |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-9000 | GPO: Single | 2 | XR Viewer & XRay Unit |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-1433 | Electrical Isolator: 1PH+N | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-9001 | GPO: Double | 8 | 2 for workstation area |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-9015 | GPO: Cleaner | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-9060 | GPO: Special: for equipment | 1 | Dental Chair & services unit |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-1006 | Voice / Data outlet: double | 1 | 1 outlet for telephone |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-1040 | Intercom | 1 | wall mounted (optional) |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-6055 | Special: task light, built in | 1 | under O/H cupboards |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-2072 | Scavenge Outlet | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-7000 | Oxygen (O2) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-7010 | Nitrous Oxide (N2O) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-7040 | Suction | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-7070 | Scavenge | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | S-11000 | Wall panel | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | Fabrics | 3060 | Wall finish | 1 |  | Vinyl | Prefinished | Splashback | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | Fabrics | 5010 | Ceiling - Plasterboard | 1 |  | Plasterboard | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | Fabrics | 9004 | Door - 1100mm | 1 | 1200mm clear opening, lockable | Solid Core/ Glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | Fabrics | 7001 | Windows | 1 | desirable |  |  |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No