## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
DISP-8 | Disposal Room, 8m2 | 8 |  |  | 24 Hours |  | The Disposal Room provides for the temporary holding of clinical waste, general waste, sharps, soiled linen and recyclables prior to removal. The Disposal Room should be located in close proximity to a handwashing basin or be provided within the room (optional) if waste will be handled in this area. The room should be lockable.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Items | [6 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
DISP-8 | Disposal Room, 8m2 | FE | FE-2850 | Basin - handwash, Type C | 1 | Default = no hand basin: optional with shroud |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
DISP-8 | Disposal Room, 8m2 | FF | FF-23925 | Trolley - soiled linen collection | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FF | FF-24102 | Waste bin - general | 2 | 240 Litre |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FF | FF-24125 | Waste bin - clinical | 1 | 240 Litre |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to hand basin, if provided |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FF | FF-6156 | Dispenser - soap | 1 | to hand basin, if provided |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FF | FF-6157 | Dispenser - medicated hand gel | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | SE | S-5019 | Exhaust | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | SE | S-6200 | Light switches | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 3060 | Wall finish | 1 | Default = no hand basin; to basin, if provided | Vinyl | Prefinished | Splashback | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 3052 | Wall finish | 1 |  | Vinyl | Prefinished | Wall vinyl to 1500 AFFL | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 4031 | Wall protection | 1 | as required | Composite | Prefinished PVC | Corner guards to 1500 AFFL | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 5030 | Ceiling - Plasterboard | 1 |  | Plasterboard | Prefinished | Drop-in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 9001 | Door - 1100mm | 1 | 1100mm clear opening, lockable, optional glazed viewing panel to door | Solid Core | Paint | Single leaf | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No