## Room Data
Standard Components - Room Data Sheet
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
DTUR-12 | Dirty Utility, 12m2 | 12 | 24 Hours | 1 - 2 intermittently |  | Sound attenuation level high, Acoustic privacy is required. | The Dirty Utility, 12m² provides a space for the decontamination and storage of bedpans, urinals and bowls, testing and disposal of patient specimens, disposal of clinical and other wastes, cleaning and holding of used equipment for collection, and holding of soiled linen for collection. Note: due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, 12m² fit out.

## Items
Standard Components - Items in room
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
DTUR-12 | Dirty Utility, 12m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
DTUR-12 | Dirty Utility, 12m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
DTUR-12 | Dirty Utility, 12m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
DTUR-12 | Dirty Utility, 12m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
DTUR-12 | Dirty Utility, 12m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
DTUR-12 | Dirty Utility, 12m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
DTUR-12 | Dirty Utility, 12m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | pull handle/push plate, closer
DTUR-12 | Dirty Utility, 12m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 5
DTUR-12 | Dirty Utility, 12m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | with wet edge
DTUR-12 | Dirty Utility, 12m2 | FFE | FIHR-038 | RACK: bowl/basin | 1 | quantity to be based on service requirements
DTUR-12 | Dirty Utility, 12m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | FIHR-029 | HOOK: equipment | 2 | optional, for clean linen bags
DTUR-12 | Dirty Utility, 12m2 | FFE | FIHR-025 | HOOK: catheter bag | 2 | optional
DTUR-12 | Dirty Utility, 12m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 3
DTUR-12 | Dirty Utility, 12m2 | FFE | FIHR-053 | RACK: pan & urinal | 1 | quantity to be based on service requirements
DTUR-12 | Dirty Utility, 12m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FIJO-196 | SHELF: stainless steel, overbench, wall mount | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FQCW-017 | BIN: waste, general, 240L | 1 | type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-12 | Dirty Utility, 12m2 | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 | type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-12 | Dirty Utility, 12m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1 | to sink
DTUR-12 | Dirty Utility, 12m2 | FFE | MMIC-095 | WASHER SANITISER: pan flusher | 1 | combined utensil/pan sanitiser may be provided
DTUR-12 | Dirty Utility, 12m2 | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1 | hot water
DTUR-12 | Dirty Utility, 12m2 | FFE | MMLA-013 | ANALYSER: urinalysis | 1 | optional
DTUR-12 | Dirty Utility, 12m2 | FFE | MMIC-097 | WASHER SANITISER: utensil washer | 1 | combined utensil/pan sanitiser may be provided
DTUR-12 | Dirty Utility, 12m2 | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 1
DTUR-12 | Dirty Utility, 12m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, for urinalysis machine
DTUR-12 | Dirty Utility, 12m2 | SE | ELPR-003 | ISOLATOR: electrical, 1ph+n | 1
DTUR-12 | Dirty Utility, 12m2 | SE | HYTP-013 | OUTLET: hot water | 2 | for washer sanitisers
DTUR-12 | Dirty Utility, 12m2 | SE | HYTP-008 | OUTLET: cold water | 2 | for washer sanitisers
DTUR-12 | Dirty Utility, 12m2 | SE | HYDR-004 | DRAIN: floor waste | 1
DTUR-12 | Dirty Utility, 12m2 | SE | HYDR-006 | DRAIN: tundish | 1 | optional, dependent on machine requirements
DTUR-12 | Dirty Utility, 12m2 | SE | ELBO-015 | SWITCH: light, single | 1
DTUR-12 | Dirty Utility, 12m2 | SE | ELGP-106 | GPO: single, special, for equipment | 2 | for washer sanitisers
DTUR-12 | Dirty Utility, 12m2 | SE | ELGP-109.1 | GPO: single, wall mounted (V) | 1 | optional, for urinalysis machine
DTUR-12 | Dirty Utility, 12m2 | SE | HYGE-028 | DEVICE: backflow prevention | 1