## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
DTUR-14 | Dirty Utility, 14m2 | 14 | 24 Hours | 1 - 2 intermittently |  | Sound attenuation level high, Acoustic privacy is required. | The Dirty Utility provides for cleaning and holding of used equipment for collection and sterilisation elsewhere, disposal of clinical and other wastes and soiled linen, testing and disposing of patient specimens and decontamination and storage of patient utensils such as pans, urinals and bowls. The Dirty Utility 14m2 may provide access doors from both sides of the room.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
DTUR-14 | Dirty Utility, 14m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | Laminate infill also acceptable. Between above bench joinery and ceiling. | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 2 | pull handle/push plate, closer | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | SE | ELBO-015 | SWITCH: light, single | 2 | two-way | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | SE | ELGP-106 | GPO: single, special, for equipment | 2 | Pan Sanitiser, Utensil Washer, or combined utensil/pan washer optional | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to hand basin | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to hand basin | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIHR-025 | HOOK: catheter bag | 2 | Above sink | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIHR-029 | HOOK: equipment | 2 | For clean linen bags, optional. | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIHR-038 | RACK: bowl/basin | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIHR-053 | RACK: pan & urinal | 2 | total of 12 pans/12 urinals | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | wet edge. Length to suit layout, refer RLS or project specific requirements. | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIJO-146 | CUPBOARD: wall mount, double door, adj shelves, waterproof carcassing | 1 | Or shelf, over bench, optional. For urinalysis equipment. | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1 | At 350mm AFFL or underbench, stainless steel cupboard. | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 | 240 or 120 litre bin. Number and size depends on Waste Management policy. | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FQCW-013 | BIN: waste, cytotoxic, 240L | 0 | Cancer treatment areas only. | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FQCW-017 | BIN: waste, general, 240L | 1 | Number and size depends on Waste Management policy. | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 | Wall mounted or trolley. | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | Elbow action levers or handsfree optional. Refer to BHWS-B (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | HYBA-046 | SINK: flushing rim | 1 | may also require pressure contol hose and flush button | No | No | Yes | Yes | No | No | Yes | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1 | Hot water & cold water. Tapware: lever tapware, fixture mounted. | No | No | Yes | Yes | Yes | Yes | Yes | No | No
DTUR-14 | Dirty Utility, 14m2 | SE | HYDR-004 | DRAIN: floor waste | 1 |  | No | No | No | No | No | No | Yes | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | HYTP-006 | HOSE: spray, pressure control | 1 | to flushing rim sink | No | No | Yes | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | SE | HYTP-008 | OUTLET: cold water | 1 |  | No | No | Yes | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | SE | HYTP-013 | OUTLET: hot water | 1 |  | No | No | No | Yes | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to sink | No | No | Yes | No | Yes | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin, handsfree optional | No | No | Yes | No | Yes | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 2 | or 3 if only one 120L bin required | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | MMIC-095 | WASHER SANITISER: pan flusher | 1 | not hardwired, combined utensil/pan washer optional | Yes | No | Yes | Yes | No | Yes | Yes | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | MMIC-097 | WASHER SANITISER: utensil washer | 1 | combined utensil/pan washer optional | Yes | No | Yes | Yes | No | Yes | Yes | No | No
DTUR-14 | Dirty Utility, 14m2 | FFE | MMLA-013 | ANALYSER: urinalysis | 1 |  | Yes | Yes | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-14 | Dirty Utility, 14m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 |  | No | No | No | No | No | No | No | No | No