## Room Template Data
Ensuite - Mental Health, Nested (ENS-MH-NE) - Room Template Properties and Room Template Data
2025-08-20
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
ENS-MH-NE | Ensuite - Mental Health, Nested | 5 | ENS-MH-B | 4 | 20.08.2025 | 24 hours | 0 |  |  |  |  | 1 patient; 1 staff assisting as required | The Ensuite - Mental Health provides a shower, toilet and handwash basin for use by consumers in a mental health inpatient unit. The nested ensuite layout is used in conjunction with the 1 Bed Room - Mental Health, Nested Ensuite (1BR-MH-NE). | ~ All fittings and fixtures used in ensuites must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible ensuite is required to be provided, anti-ligature fittings may require a performance solution to be provided in order for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~ This Standard Component may be configured to be accessed from a corridor instead of directly from a bedroom. Additional requirements to suit this scenario (e.g. access control, occupancy indicators, etc.) are to be confirmed based on local jurisdictional policies. ~If provided, all glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific the mental health environment (i.e. non-acute, acute, intensive care). ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ The ensuite door configuration is to be confirmed at project level to suit service requirements and jurisdictional policies (options include solid door, anti-ligature sliding door, lightweight saloon doors, without door, provision of undercut/overcut). The door in this Standard Component is shown with an angled cut down at top and optional cut at bottom. Alternatively magnetic load release leaf/saloon style doors may be provided. Anti-ligature sliding doors may also be considered based on risk assessment. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof and anti-ligature requirements when used together. ~ The inclusion of door top or top and side anti-ligature alarms connected to the emergency call/duress systems may be assessed at project level to suit service requirements. ~ Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ Unique considerations for Intensive Care and Child and Adolescent areas are to be confirmed at project level to suit jurisdictional policies ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate an institutional feel. ~ Coat hooks are shown as optional. Some jurisdictions do not support the provision of coat hooks (e.g. Victoria), refer to jurisdictional policies for guidance; in areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered ~ Anti-pick caulking is recommended for finishing between surfaces. ~ Provision of motion sensor lighting or switched lighting to be considered at project level. | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-08-20
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
ENS-MH-NE | Ensuite - Mental Health, Nested | D+W | DOHI-003.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 1 | with angled cut down from top; may alternatively be provided as magnetic leaf/saloon style doors
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FIBM-107 | MIRROR: fixed, safety glass, toughened and laminated, frameless, recessed, tamper proof, anti-ligature | 1 | 1 |  | material to be confirmed at project level to suit service requirements
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FIDI-283 | HOLDER: soap/shampoo, wall recessed, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FIDI-302 | DISPENSER: toilet paper, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FIRT-124 | GRAB RAIL: toilet, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FIRT-154 | GRAB RAIL: shower, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FQGE-102 | CURTAIN: shower | 1 | 1 |  | optional
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | HYBA-152 | BASIN: type C, handwashing, anti-ligature, with integral single shelf | 1 | 1 |  | location of thermostatic mixing valve to be determined based on need to restrict consumer access; typically provided behind a lockable panel in external corridor
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | HYSH-006 | SHOWER: fixed rose, wall mounted, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | HYTP-002 | FLUSH BUTTON: toilet suite | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | HYTP-069 | TAPWARE: basin, tap set, wall mounted, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | HYTP-263 | TAPWARE: shower, tap set, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | HYWC-036.02 | TOILET SUITE: patient, anti-ligature, tamper proof, concealed cistern | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FIDI-257 | DISPENSER: soap, wall mounted, anti-ligature | 1 | 1 |  | to basin
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FIHR-027 | HOOK: coat, collapsible, tamper proof, anti-ligature | 2 | 1 |  | optional; some jurisdictions do not support the provision of coat hooks (e.g. Victoria), refer to jurisdictional policies for guidance; in areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered
ENS-MH-NE | Ensuite - Mental Health, Nested | FFE | FIRT-066 | TRACK: curtain, shower, recessed/collapsible, anti-ligature | 1 | 1 |  | optional
ENS-MH-NE | Ensuite - Mental Health, Nested | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | based on a risk assessment tiles may also be acceptable
ENS-MH-NE | Ensuite - Mental Health, Nested | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | based on a risk assessment tiles may also be acceptable
ENS-MH-NE | Ensuite - Mental Health, Nested | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
ENS-MH-NE | Ensuite - Mental Health, Nested | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
ENS-MH-NE | Ensuite - Mental Health, Nested | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting | to be tiles if tiled floor provided
ENS-MH-NE | Ensuite - Mental Health, Nested | SER | HYDR-022 | DRAIN: floor waste, round, tamper proof, anti-ligature | 2 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | SER | HYDR-082 | DRAIN: clear out, round, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-MH-NE | Ensuite - Mental Health, Nested | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | to toilet
ENS-MH-NE | Ensuite - Mental Health, Nested | SER | HYDR-201.01 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-MH-NE | Ensuite - Mental Health, Nested | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
ENS-MH-NE | Ensuite - Mental Health, Nested | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
ENS-MH-NE | Ensuite - Mental Health, Nested | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside room
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
1BR-IC
1BR-BA