## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
HYDP | Hydrotherapy Pool | 90 |  | Up to 12 | 7am to 8pm, daily |  | Hydrotherapy Pool for patient rehabilitation and exercise under supervision. Pool size 15m x 6 m (not including pool surrounds). Pool and surrounds to comply with AS 3979 - Hydrotherapy Pools. Additional Design Considerations: - Depth 0.9 metres to 1.5 metres - gradual slope; Deep end may be reduced if paediatric use is likely to be frequent - Wet deck - single channel; - Temperature of water - 33 - 34 degrees; - Temperature of air to be no more than 10 degrees below water temperature - Water to be earthed - Pool surface - tiled, non-slip; ensure a high level of slip resistance to tiles on the ramp; vertical surfaces of tiling do not need to be slip resistant - Glazing to pool walls recommended - Ramp access with handrail & stair access with handrails - Pool handrails required - not recessed type - Pool blanket may be required (insulation for energy conservation) - Disinfection system to be advised - Pool hydraulic hoist may be required - Underwater pressure jets for therapeutic purposes is optional

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
HYDP | Hydrotherapy Pool | Fabrics | 1175 | Floor finish | 1 | Metz' 245x122 or 'Granito' 200x200 are suitable | Tiles | Non-slip | Ceramic | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | Fabrics | 2145 | Skirting | 1 | max 25mmH | Tiles | To match floor | Coved | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | Fabrics | 3090 | Wall finish | 1 |  | Tiles | Glazed |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | Fabrics | 5040 | Ceiling - Fibre Cement | 1 |  | Fibre cement | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | Fabrics | 7001 | Windows | 1 | Desirable |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | Fabrics | 7030 | Observation | 1 | Observation windows as required | Alum/ Glass | Powdercoat | Internal window, door height | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | Fabrics | 9001 | Door - 1100mm | 1 | to Change Rooms/ Cleaner/ Plant areas; lockable | Solid Core | Paint | Single leaf | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | Fabrics | 9003 | Doors | 1 | alternative Exit if required by BCA; 910mm clear opening, lockable | Alum/ Safety glass | Powdercoat/ paint | Single leaf, fully glazed | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | Fabrics | 9120 | Door - 1400mm | 1 | to Lobby/ Waiting & Exit; 1500mm clear opening, lockable, restricted access | Alum/ Safety glass | Powdercoat/ paint | 1 1/2 leaf, fully glazed | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FE | FE-40630 | Pool blanket - auto operated | 1 | optional |  |  |  | Yes | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FE | FE-41910 | Public address system | 1 | announcements, music |  |  |  | Yes | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FF | FF-1000 | Bench seat | 2 | to concourse, under lockers, optional |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FF | FF-12600 | Locker - 4 tier (1/4 size) | 8 | to concourse, on bench seat, optional |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FF | FF-17715 | Hoist - pool, hydraulic | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FF | FF-4800 | Curtain track - shower (straight) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FF | FF-5300 | Curtain - shower | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | S-1140 | Public address system | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | S-4010 | Cold water: outlet | 1 | for washing down concourse |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | S-4033 | Floor waste | 18 | every 3-4 metres on concourse |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | S-5005 | Air conditioning: special | 1 | to prevent condensation; ensure all ductwork & grilles are corrosion resistant |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | S-6000 | General fluorescent | 1 | to avoid reflection on water; avoid luminaires over actual water area (for maintenance) |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | S-8080 | Emergency call | 4 | 1 each side of pool |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | S-9000 | GPO: Single | 4 | waterproof, chlorine resistant |  |  |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | S-9060 | GPO: Special: for equipment | 1 | motorised pool blanket if required |  |  |  | No | No | No | No | No | No | No | No | No