## Room Template Data
Interview Room - Mental Health (INTV-MH) - Room Template Properties and Room Template Data
2025-08-20
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
INTV-MH | Interview Room - Mental Health | 14 | INTF-MH | 2 | 18.08.2025 | Up to 24 hours | 0 |  |  |  |  | up to 6 persons | The Interview Room - Mental Health (may be referred to on projects as a Dialogue Room) provides the space and amenities for interviews, counselling, collaborative care planning and small support network discussions. | ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings of a type manufactured and marketed as anti-ligature (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. Anti-ligature fittings may require a performance solution to be provided for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. Inclusion and size of a vision panel to be confirmed to suit service requirements. Privacy film may be applied to the vision panel as required. ~ A second door is required for safety and security. The location of the second door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ Provision of a workstation is dependent on service requirements (e.g. for computer based assessments to be undertaken). Impact on furniture arrangement when workstation is included must be considered to support a positive dynamic between staff and consumers, and encourage participation of consumers as equal partners in care. ~ Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ Unique considerations for Intensive Care and Child and Adolescent areas are to be confirmed at project level to suit jurisdictional policies ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate an institutional feel. ~ Nearby access to a beverage bay or water fountain is recommended. ~ Natural light and external outlook is desirable. Consider placement of windows and room orientation to suit privacy requirements. | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-08-20
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
INTV-MH | Interview Room - Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side as required
INTV-MH | Interview Room - Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish
INTV-MH | Interview Room - Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 1 | requirements for glazing in vision panel to be confirmed to suit the mental health environment
INTV-MH | Interview Room - Mental Health | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 3 | External - Window 1 | optional; natural light and external outlook is desirable; consider placement and room orientation for patient privacy; requirements for glazing to be confirmed to suit the mental health environment
INTV-MH | Interview Room - Mental Health | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 3 | External - Window 1
INTV-MH | Interview Room - Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to corridor side as required
INTV-MH | Interview Room - Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional; provision dependent on frame material and finish
INTV-MH | Interview Room - Mental Health | D+W | DOHI-003.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 2 | secondary egress
INTV-MH | Interview Room - Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to room side
INTV-MH | Interview Room - Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to room side
INTV-MH | Interview Room - Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 2 | optional; provision to suit security and egress requirements
INTV-MH | Interview Room - Mental Health | D+W | AFDFI-026 | DOOR GLAZING FINISH: vision panel, privacy film | 1 | 1 | Internal - Door 1 | optional; as required to suit privacy requirements
INTV-MH | Interview Room - Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional; provision to suit security and egress requirements
INTV-MH | Interview Room - Mental Health | FFE | FIBM-020 | WHITEBOARD: fixed, magnetic, tamper proof, anti-ligature | 1 | 1
INTV-MH | Interview Room - Mental Health | FFE | FIBM-057 | NOTICEBOARD: fixed, fabric covered, tamper proof, anti-ligature | 1 | 1
INTV-MH | Interview Room - Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 2 | 1
INTV-MH | Interview Room - Mental Health | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1
INTV-MH | Interview Room - Mental Health | FFE | FQBS-354 | LOUNGE: ottoman | 2 | 1
INTV-MH | Interview Room - Mental Health | FFE | FQDW-104.02 | WORKSTATION: straight, fixed height, 720H, 750D x 1200W | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1
INTV-MH | Interview Room - Mental Health | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
INTV-MH | Interview Room - Mental Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 1 | 1 | Floor Skirting
INTV-MH | Interview Room - Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
INTV-MH | Interview Room - Mental Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | if tamper proof and anti-ligature finish required, flush set ceiling to be provided
INTV-MH | Interview Room - Mental Health | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
INTV-MH | Interview Room - Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1
INTV-MH | Interview Room - Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1
INTV-MH | Interview Room - Mental Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 3
INTV-MH | Interview Room - Mental Health | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
1BR-IC
1BR-BA