## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
LAUN-MH | Laundry - Mental Health | 6 |  | 1 - 2 | 24 Hours |  | Domestic style laundry for use by mental health patients with staff supervision. The room will include a bench, laundry tub, domestic washing machine and dryer and ironing facilities. All fittings to be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a standard nominal thickness of 10.38mm, or equivalent approved. Door and joinery hardware should not provide ligature points.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
LAUN-MH | Laundry - Mental Health | Fabrics | 1020 | Floor finish | 1 |  | Vinyl, non-slip | Safety | Seamless, coved | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | Fabrics | 3052 | Wall finish | 1 | tiles also acceptable | Vinyl | Prefinished | Wall vinyl to 1500 AFFL | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | Fabrics | 5021 | Ceiling - Plasterboard | 1 |  | Plasterboard | Paint, washable | Water resistant, flush set, suspended | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | Fabrics | 7031 | Observation | 1 | observation window | Alum/ Safety glass | Powdercoat/ paint | Internal window | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | Fabrics | 9006 | Door - 1100mm | 1 | 910mm clear opening, lockable; anti-hang door harware | Solid Core/ Safety glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | FE | FE-18400 | Dryer - tumble, domestic | 1 | wall mounted |  |  |  | Yes | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | FE | FE-29200 | Iron - electric | 1 | inside cupboard |  |  |  | Yes | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | FE | FE-4045 | Tapware - elbow mixer | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | FE | FE-49400 | Sink - laundry, single | 1 | warm water, with overflow drain |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
LAUN-MH | Laundry - Mental Health | FE | FE-60650 | Washing machine - domestic | 1 | provide themostatic mixing valve to hot water or supply warm water |  |  |  | Yes | No | Yes | Yes | Yes | No | Yes | No | No
LAUN-MH | Laundry - Mental Health | FF | FF-1050 | Bench - laminate | 1 | with inset laundry tub |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | FF | FF-1460 | Bracket - wall | 1 | for dryer |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | FF | FF-1505 | Cabinet - ironing board | 1 | lockable, with integral ironing board |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | FF | FF-23956 | Trolley - laundry, basket | 1 | under bench |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | FF | FF-4410 | Cupboard: under bench | 1 | under laundry, lockable |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | FF | FF-44812 | Overbench double door (785w) | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-1086 | General fluorescent: vandal proof | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-1088 | RCD device | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-4000 | Hot water: outlet | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-4010 | Cold water: outlet | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-4033 | Floor waste | 1 | vandal proof |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-5000 | Airconditioning | 1 | with vandal proof outlet |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-5019 | Exhaust | 1 | extra steam/ heat extraction to room for dryer; vandal proof outlet |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-9000 | GPO: Single | 3 | washer, dryer, ironing cabinet |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-9001 | GPO: Double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
LAUN-MH | Laundry - Mental Health | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No