## Room Data
Standard Components - Room Data Sheet
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
MED-14 | Medication Room, 14m2 | 14 | 24 Hours | 1 - 2 staff intermittently |  |  | The Medication Room, 14m² is used for the secure storage of medications, including intravenous fluids, and a small amount of medication-related clean consumables. The room may provide storage for drugs of dependence in accordance with relevant legislation. Controlled temperature and humidity is required for medication storage and internal temperatures should not rise above 25°C. Secured staff only access to the room is required. The provision and placement of CCTV cameras is dependent on jurisdictional policies. Refer to project specific requirements for the provision of automated medication management systems.

## Items
Standard Components - Items in room
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
MED-14 | Medication Room, 14m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
MED-14 | Medication Room, 14m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 9
MED-14 | Medication Room, 14m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
MED-14 | Medication Room, 14m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
MED-14 | Medication Room, 14m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MED-14 | Medication Room, 14m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 4 | extent dependent on type and height storage solution
MED-14 | Medication Room, 14m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
MED-14 | Medication Room, 14m2 | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 1
MED-14 | Medication Room, 14m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
MED-14 | Medication Room, 14m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 1 | extent dependent on type and height storage solution
MED-14 | Medication Room, 14m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
MED-14 | Medication Room, 14m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
MED-14 | Medication Room, 14m2 | FFE | FIJO-157 | CUPBOARD: wall mount, single door, adj shelves, lockable | 1
MED-14 | Medication Room, 14m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
MED-14 | Medication Room, 14m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
MED-14 | Medication Room, 14m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
MED-14 | Medication Room, 14m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
MED-14 | Medication Room, 14m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
MED-14 | Medication Room, 14m2 | FFE | MMGE-087 | SAFE: dangerous drugs, medium | 1 | size and quantity to be based on service requirements
MED-14 | Medication Room, 14m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
MED-14 | Medication Room, 14m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
MED-14 | Medication Room, 14m2 | FFE | FIJO-108 | CUPBOARD: drawer unit, baskets, 3 x Wire (400mm wide) | 5
MED-14 | Medication Room, 14m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
MED-14 | Medication Room, 14m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
MED-14 | Medication Room, 14m2 | FFE | ITSE-012 | CAMERA: CCTV | 1 | optional, provision and placement dependent on local policies
MED-14 | Medication Room, 14m2 | FFE | MMGE-034 | FRIDGE: drugs, large | 1 | size and quantity to be based on service requirements
MED-14 | Medication Room, 14m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
MED-14 | Medication Room, 14m2 | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
MED-14 | Medication Room, 14m2 | FFE | FQSM-046 | SHELVING: storage solution, 600W x 400D x 2100H nom., wire, mobile | 3 | type and quantity of storage options to be determined based on service requirements
MED-14 | Medication Room, 14m2 | FFE | FQCW-061 | BIN: waste, pharmaceutical | 1
MED-14 | Medication Room, 14m2 | FFE | FQSM-048 | SHELVING: storage solution, shelving, 600W x 400D x 2100H nom., wire, mobile | 2 | type and quantity of storage options to be determined based on service requirements
MED-14 | Medication Room, 14m2 | FFE | FIDI-052 | DISPENSER: sticker roll | 1 | optional
MED-14 | Medication Room, 14m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to drug fridge, for temperature monitoring
MED-14 | Medication Room, 14m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 2x optional, for future provision of automated dispensing cabinets
MED-14 | Medication Room, 14m2 | SE | LIFX-008 | LIGHT: task light, built in | 1 | under wall mounted joinery
MED-14 | Medication Room, 14m2 | SE | ELBO-015 | SWITCH: light, single | 2 | 1 x general room lighting, 1 x task light
MED-14 | Medication Room, 14m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
MED-14 | Medication Room, 14m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | optional, for future provision of automated dispensing cabinets
MED-14 | Medication Room, 14m2 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to drug fridge
MED-14 | Medication Room, 14m2 | SE | ITSE-038 | READER: access control, general | 1