## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
MEET-L-55 | Meeting Room, 55m2 | 55 |  |  | Available up to 24 Hours | Sound attenuation level high, Acoustic privacy is required. | The large Meeting Room will provide videoconferencing facilities for staff and client meetings. It is a multipurpose room also used for training or educational purposes. The room should be located away from high traffic and noise areas. An operable wall will allow the room to be sub-divided, so that two separate meetings can be run simultaneously. For use in mental health applications, an alternative egress door should be provided and equipment recessed into walls where possible; finishes, fittings & fixtures and furniture should be suitable for mental health patients. For Mental Health rooms, all glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a standard nominal thickness of 10.38mm, or equivalent approved. Integration of Video-conference equipment should be considered including the following: - Lectern design - Room and VC Control (AMX, Creston, Joey etc.) - Room sound system - Room microphone system (dual, wireless, ceiling or combination) - Display system (e.g. projector, monitor or monitors) - AV equipment (matrix switch, amp, secondary camera etc.) Acoustics: Sound attenuation level high; Acoustic privacy required; discussions within the room should not be heard in adjacent rooms or corridor; reverberation time RT60 in the room ideally less than 250ms; background noise (from HVAC or other sources) should be kept to a minimum, below 40dBA; avoid parallel hard surfaces in the room; acoustic panelling may be considered. Additional design requirements: - table should be positioned so that all chairs face the camera; tables may be small modular type located together or oval - high level of lighting is required in the room to illuminate faces in view of the camera; avoid bright spots, shadows or dark patches; the front light fittings should be 45 degrees above the subject&apos;s horizontal sightline; track lighting with halogen lamps may be considered - room decor should avoid white or pastel colours for optimal picture quality; soft furnishings should avoid busy patterns in camera view - hard surfaces should be covered to minimise echo; - provide data and ISDN (Onramp2) connections and 2 DGPOs for the videoconferencing unit in addition to other power/data provisions in the room; verify locations on site - Network termination boxes (NT1), if required for local areas, should be located within the room; if adjacent rooms are sharing lines, no patch panels should be used, outlets (sBus) should be parallel & active

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Items | [6 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
MEET-L-55 | Meeting Room, 55m2 | FE | FE-11100 | Computer - laptop | 2 | for presentations; optional |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FE | FE-34800 | Microphone | 2 | videoconference unit component; will requrie a min of 2 for 35m2 room - may require 1 microphone between every 2 chairs; on table; may also be ceiling mounted |  |  |  | Yes | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FE | FE-41350 | Projection screen - ceiling, auto | 1 | optional |  |  |  | Yes | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FE | FE-41400 | Projector | 1 | ceiling mounted; optional |  |  |  | Yes | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FE | FE-54510 | Telephone - handset, standard | 2 | 1 wall phone outside room entry |  |  |  | No | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FE | FE-7722 | Camera - video-conferencing | 1 | 2nd camera optional; for video stream switching |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FE | FE-7722 | Camera - video-conferencing | 1 | part of videoconferencing unit; mounted to monitor/s or wall mounted |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FE | FE-7719 | Monitor - LCD | 2 | videoconference unit component; Plasma, 50" min, high resolution screen with HDMI (High Definition Multimedia Interface); 2nd screen optional |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FE | FE-7720 | Speakers - video-conferencing, wall mounted | 2 |  |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FE | FE-6466 | Telephone - teleconference | 2 |  |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FE | FE-7721 | Video-conferencing system | 2 |  |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-1050 | Bench - laminate | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-17360 | Pinboard - fabric covered | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-2060 | Chair - meeting room | 44 | some with arms |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-3350 | Clock - battery operated | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-4350 | Cupboard - tall | 1 | for video-conferencing equipment; optional |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-4410 | Cupboard - under bench | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-5100 | Curtain - blackout | 1 | optional; or black-out blinds for audiovisual presentations; |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-7513 | Bracket LCD monitor | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-7516 | External window dressing, blackout | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-5824 | Waste bin - general | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-24405 | Whiteboard - magnetic | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-4490 | Cupboard - double door, freestanding, lockable | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-12200 | Lectern | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FF | FF-16025 | Operable wall | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-9001 | GPO: Double | 1 | videoconferencing unit; verify location before installation |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-9001 | GPO: Double | 5 | on walls; 3-VC unit; 2 may be provided on wall or in floor services box as required |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-9015 | GPO: Cleaner | 1 | as required |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-9011 | GPO: Emergency power, double (H) | 1 | videoconferencing unit; verify location before installation |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-9060 | GPO: Special: for equipment | 1 | in ceiling for data projector; optional |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-1005 | Voice / Data outlet: single | 1 | in ceiling for data projector; optional |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-1006 | Voice / Data outlet: double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-1007 | Voice / Data outlet: triple | 3 | on wall for VC unit (min requirement for VC is 1-triple outlet); 1 outlet for IP connectivity for videoconferencing unit; ISDN (Onramp2) connection, ISDN NT box only if required; network terminator boxes (NT1) to be located within the room; equipment to be directly connected, no patch panels; verify location before installation |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-1090 | TV: MATV | 2 | 1 to each monitor |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-1387 | Floor services box: flush mount | 2 | for data and power, optional; verify location before installation |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE-Req | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-6000 | General fluorescent | 1 | lighting to achieve 600 lux to faces in view of the camera (may range from 540-750 lux); lighting to be even to room, avoiding bright spots, dark patches and shadows in the room; colour temp of light fittings 3000-3500K (5000-5600K if blackout cannot be achieved); refer to Special Requirements for additional comments |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE-Req | S-6000 | General fluorescent | 1 | lighting to achieve 600 lux to faces in view of the camera (may range from 540-750 lux); lighting to be even to room, avoiding bright spots, dark patches and shadows in the room; colour temp of light fittings 3000-3500K (5000-5600K if blackout cannot be achieved); refer to Special Requirements for additional comments |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-6200 | Light switches | 4 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-6110 | Downlights: dimmable | 1 | for audiovisual presentations; refer to Special Requirements for additional comments |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE-Req | S-6110 | Downlights: dimmable | 1 | for audiovisual presentations; refer to Special Requirements for additional comments |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-8080 | Emergency call | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | S-10005 | Duress alarm | 2 | optional |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | Fabrics | 1149 | Floor finish | 1 |  | Carpet | 90/10 Wool/ Nylon | Broadloom, 48 oz. | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | Fabrics | 3000 | Wall finish | 1 | Decor to be light/neutral, avoid white and pastel colours, free from patterning, no grey/ bue-grey shades for optimal picture quality | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | Fabrics | 1126 | Wall finish | 1 | may be required depending on room acoustics | Acoustic panels | Prefinished |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | Fabrics | 5060 | Ceiling - Acoustic | 1 |  | Acoustic | Prefinished | Drop-in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | Fabrics | 8000 | Door protection | 1 | Equal to Acrovyn | Vinyl | Prefinished | Kickplate, 300mm high | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | Fabrics | 9128 | Door - 1200mm | 1 | 1350 mm clear opening, with cover to observation panel; lock set | Solid Core/ Glass | Paint | 1 1/2 leaf, observation panel | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | Fabrics | 7001 | Windows | 1 | not essential; if provided, preferrabley not on a wall in front of the camera |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | Fabrics | 2010 | Skirting | 1 |  | Vinyl | Prefinished | Feather edged, 150 mmH | No | No | No | No | No | No | No | No | No