## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
MOR-AU | Mortuary - Autopsy Room | 30 |  | Up to 4 | Available 24 Hours |  | Room for undertaking post mortem examinations. The Autopsy Room should be located adjacent to the Body Cool Store and have ready access to a clean-up area. Additional Design Considerations - Doors to be sealed for odours - Post mortem table to have water flushing system - An observation area is optional

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
MOR-AU | Mortuary - Autopsy Room | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | Fabrics | 3052 | Wall finish | 1 |  | Vinyl | Prefinished | Wall vinyl to 1500 AFFL | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | Fabrics | 5010 | Ceiling - Plasterboard | 1 |  | Plasterboard | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | Fabrics | 7030 | Observation | 1 | observation window/s | Alum/ Glass | Powdercoat | Internal window, door height | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | Fabrics | 9128 | Door - 1200mm | 1 | 1400mm clear opening | Solid Core/ Glass | Paint | 1 1/2 leaf, observation panel | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FE | FE-3100 | Basin - scrub, Type A | 1 | refer to BHWS-A (sim); sensor taps |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
MOR-AU | Mortuary - Autopsy Room | FE | FE-40404 | Tapware - sensor | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FE | FE-45600 | Hose reel - retractable | 1 |  |  |  |  | No | No | Yes | No | Yes | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FE | FE-49000 | Sink - 500x450x250D | 1 | sensor taps, hot water |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
MOR-AU | Mortuary - Autopsy Room | FE | FE-49205 | Sink - draining | 1 | in bench, sensor taps, hot water |  |  |  | No | No | Yes | Yes | Yes | No | Yes | No | No
MOR-AU | Mortuary - Autopsy Room | FE | FE-53050 | Saw - surgical | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FE | FE-54100 | Table - post mortem | 1 | & medical gases to pedestal |  |  |  | Yes | No | Yes | Yes | Yes | No | Yes | No | No
MOR-AU | Mortuary - Autopsy Room | FE | FE-54520 | Telephone - handset, handsfree | 1 | wall telephone |  |  |  | No | Yes | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FE | FE-5857 | Light - procedures small, ceiling | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FE | FE-68700 | Xray viewer - 2 screen | 1 | recessed |  |  |  | Yes | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-1010 | Bench - stainless steel | 1 | with wet edge & draining sink |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-1470 | Bracket - sharps | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-1550 | Cabinet - instrument | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-19700 | Sharps bin | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-19820 | Shelf - SS, under | 3 | under SS bench |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-21730 | Stool - operating, mobile | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-21950 | Suction adapter | 1 | to table |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-23950 | Trolley | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-24125 | Waste bin - clinical | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-24405 | Whiteboard - magnetic | 1 | 900x900, optional |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-3350 | Clock - battery operated | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-6156 | Dispenser - soap | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-1000 | Telephone: PABX | 1 | wall phone, handsfree |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-1040 | Intercom | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-4030 | Drainage | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-4033 | Floor waste | 2 | 1 under sink, with removable filtered trap |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-5019 | Exhaust | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-7030 | Tool Air | 1 | to table |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-7040 | Suction | 1 | to table |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-9000 | GPO: Single | 5 | 2-table; 2-bench; 1-wall |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-9001 | GPO: Double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | S-9010 | GPO: Emergency power, single (V) | 2 | 1-table; 1-bench |  |  |  | No | No | No | No | No | No | No | No | No