## Room Data
Standard Components - Room Data Sheet
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
MOR-BH | Mortuary - Body Holding | 22 | 24 Hours | 1 - 2 staff intermittently |  |  | The Mortuary - Body Holding provides refrigerated storage for the temporary holding of bodies with an adjacent area to transfer a body from a trolley into storage. The room can be configured with refrigerated cabinets or as a cool room depending on service requirements. The Mortuary - Body Holding should be located with ready access to the Mortuary - Viewing Room.

## Items
Standard Components - Items in room
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
MOR-BH | Mortuary - Body Holding | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1
MOR-BH | Mortuary - Body Holding | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
MOR-BH | Mortuary - Body Holding | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
MOR-BH | Mortuary - Body Holding | FA | WLPR-021 | WALL PROTECTION: crash rail, at 900 AFFL | 2
MOR-BH | Mortuary - Body Holding | FA | WLPR-006 | WALL PROTECTION: corner guards | 1
MOR-BH | Mortuary - Body Holding | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
MOR-BH | Mortuary - Body Holding | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MOR-BH | Mortuary - Body Holding | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
MOR-BH | Mortuary - Body Holding | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
MOR-BH | Mortuary - Body Holding | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
MOR-BH | Mortuary - Body Holding | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 5
MOR-BH | Mortuary - Body Holding | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
MOR-BH | Mortuary - Body Holding | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
MOR-BH | Mortuary - Body Holding | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
MOR-BH | Mortuary - Body Holding | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
MOR-BH | Mortuary - Body Holding | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
MOR-BH | Mortuary - Body Holding | FFE | FIHR-029 | HOOK: equipment | 1 | for lifter straps/slings
MOR-BH | Mortuary - Body Holding | FFE | MMGE-133 | TROLLEY: mortuary, hydraulic | 1 | bariatric capacity to be confirmed based on service requirements
MOR-BH | Mortuary - Body Holding | FFE | HYBA-010 | BASIN: handwash, Type B | 1
MOR-BH | Mortuary - Body Holding | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
MOR-BH | Mortuary - Body Holding | FFE | HYTP-003 | HOSE REEL: retractable | 1
MOR-BH | Mortuary - Body Holding | FFE | MMGE-183 | FRIDGE: body holding, triple tier | 3 | bariatric capacity to be confirmed based on service requirements; power and BMS requirements to be confirmed by project
MOR-BH | Mortuary - Body Holding | FFE | MMBE-070 | LIFTER: patient, ceiling mounted, motor and sling component, mortuary | 1 | mobile lifter may be used, bariatric capacity to be confirmed based on service requirements; control may be suspended from motor or wall mounted depending on model
MOR-BH | Mortuary - Body Holding | FFE | MMBE-071 | LIFTER: patient, ceiling mounted, track, linear, mortuary | 1 | mobile lifter may be used, bariatric capacity to be confirmed based on service requirements
MOR-BH | Mortuary - Body Holding | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | temperature monitoring, IP rated to suit AS/NZS wet zone requirements, 1 to each refrigerator, BMS requirements to be confirmed by project
MOR-BH | Mortuary - Body Holding | SE | ITBU-001 | ALARM: equipment monitoring, temperature | 1 | temperature monitoring, alarm and BMS requirements to be confirmed by project
MOR-BH | Mortuary - Body Holding | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to lifter
MOR-BH | Mortuary - Body Holding | SE | HYDR-004 | DRAIN: floor waste | 1
MOR-BH | Mortuary - Body Holding | SE | HYTP-012 | OUTLET: hosecock, cold water | 1
MOR-BH | Mortuary - Body Holding | SE | ELBO-015 | SWITCH: light, single | 1 | IP rated to suit AS/NZS wet zone requirements
MOR-BH | Mortuary - Body Holding | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | IP rated to suit AS/NZS wet zone requirements
MOR-BH | Mortuary - Body Holding | SE | ELGP-106 | GPO: single, special, for equipment | 3 | 1 to each refrigerator; required to be emergency power/generator backed. IP rated to suit AS/NZS wet zone requirements