## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | 25 |  | 1 patient, 1- visitors, Up to 6-8 staff | 24 Hours | Acoustic privacy is required | An enclosed single Bed Bay for a patient requiring critical care nursing and medical treatment, suitable for Levels 5 & 6 health care facilities; Visual access to Staff Station is required; Screen curtains are required for patient privacy. Maximum natural light is required to patient beds. Acoustics: Acoustic privacy is required. Cardiac Protected Electrical Area

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Items | [6 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FE | FE-15985 | Dialysis station | 1 | with RO water outlet & tundish drain |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FE | FE-3100 | Basin - scrub, Type A | 1 | refer to BHWS-A (sim) |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FE | FE-31700 | Light - examination, ceiling | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FE | FE-36050 | Monitor - cardiac | 1 | on services pendant |  |  |  | Yes | Yes | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FE | FE-3730 | Bed - ICU, electric | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FE | FE-54520 | Telephone - handset, handsfree | 1 | wall phone |  |  |  | No | Yes | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FE | FE-9700 | Clock - analogue, electric | 1 | master clock system |  |  |  | Yes | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FE | FF-5547 | Patient entertainment | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FE | FE-5859 | Services pendant - 2 arm | 1 |  |  |  |  | Yes | Yes | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-1090 | Bench - laminate, free standing | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-12300 | Linen carrier - dirty, single | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-1252 | Blind - Venetian integral | 4 | to windows, controls to both sides of internal observation windows |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-1470 | Bracket - sharps | 1 | mounted on trolley |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-150 | Air flowmeter | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-16200 | Table - overbed | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-16250 | Oxygen flowmeter | 4 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-19700 | Sharps bin | 1 | mounted on trolley |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-20000 | Shelving unit - adjustable | 1 | near basin |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-21700 | Stool - adjustable, mobile, high | 1 | for staff |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-21950 | Suction adapter | 4 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-2200 | Chair - recliner | 1 | patient - intermittent use |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-22000 | Suction bottle | 4 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-22050 | Suction bottle carrier | 1 | mobile |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-23950 | Trolley | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-24400 | Whiteboard | 1 | 600 x 600 |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-2610 | Chair - visitor, stackable | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-4600 | Curtain track - bed screen | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-5000 | Curtain - bed screen | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-6152 | Dispenser - disposable glove | 1 | near entry |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-6156 | Dispenser - soap | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-8070 | Flowchart stand - mobile | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-5825 | Bracket - patient entertainment, ceiling | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-5975 | Waste bin - clinical | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | FF | FF-5591 | Bracket - cardiac monitor | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-9000 | GPO: Single | 12 | to services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-9010 | GPO: Emergency power, single (V) | 12 | to services pendant (2-UPS) |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-9001 | GPO: Double | 4 | 2 - walls; 2-ceiling services box |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-9015 | GPO: Cleaner | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-9030 | Cardiac protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-9011 | GPO: Emergency power, double (H) | 1 | dialysis station |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-9060 | GPO: Special: for equipment | 3 | TV, proc light, clock |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-1006 | Voice / Data outlet: double | 1 | services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-1006 | Voice / Data outlet: double | 2 | 1-wall; 1-ceiling services box, 1 outlet on each panel for telephone |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-1090 | TV: MATV | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-1120 | Monitor connection facilities and cabling | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-4037 | Tundish drain | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-4045 | Reverse osmosis (RO) water outlet | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-6060 | Special: night lights | 1 | wall washers |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-8000 | Patient/ Staff call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-8005 | Patient call handset | 1 | call button on the handset |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-8010 | Staff/ Nurse assist call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-7000 | Oxygen (O2) | 4 | to services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-7020 | Medical Air (MA) | 2 | to services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-7040 | Suction | 4 | to services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | SE | S-11050 | Column | 1 | for power/ data, ceiling suspended |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 3060 | Wall finish | 1 | to basin | Vinyl | Prefinished | Splashback | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 3092 | Wall protection | 1 |  | MDF | Laminate | Bed protection wall panel | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 5010 | Ceiling - Plasterboard | 1 |  | Plasterboard | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 9002 | Door - 910mm | 1 | additional door to adjoining space optional | Solid Core/ Glass | Paint | Single leaf, half glazed | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 9330 | Door - sliding | 1 |  | Alum/ Safety glass | Powdercoat/ paint | Triple leaf, fully glazed, sliding | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 7001 | Windows | 1 | desirable |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 7055 | Observation | 1 | to partition walls, with integral Venetians | Alum/ Glass | Powdercoat | Internal window, double glazed | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
PBCE-25 | Patient Bay - Critical (Enclosed), 25m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No