## Room Data
Standard Components - Room Data Sheet
Date of issue: 26.04.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | 9 | 7am to 9pm, daily | 1 patient, 1 visitor, 1-2 staff |  |  | The Patient Bay - Renal Dialysis is for patients receiving haemodialysis therapy. Treatments for each patient may take from 3 to 6 hours, occurring up to 3 days per week. A staff handwashing basin will be provided for each 4 bays and the Patient Bay will have, wherever possible, clear line of sight to a staff station. Access to natural light and views is required. Furniture and furnishings should provide a high level of patient comfort and amenity.

## Items
Standard Components - Items in room
Date of issue: 26.04.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent; a higher slip rating may be required depending on local WHS policies
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | optional, to side walls if provided
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 2 | optional, to side walls if provided
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | DWWH-005 | WINDOW | 1 | access to natural light and external outlook essential
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FIHR-019 | BRACKET: for suction bottle | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | DWWD-004 | BLIND: roller | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FQGE-010 | CURTAIN: privacy screen | 2
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FQTA-013 | TABLE: overbed | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MGFP-004 | FLOWMETER: oxygen | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MMGE-002 | ADAPTER: suction | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MMGE-100 | SUCTION BOTTLE | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MMGE-023 | CHAIR: recliner, clinical, electric | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MMGE-049 | MACHINE: dialysis | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MMGE-096 | STATION: combination dialysis connection point and waste water tundish | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1 | optional
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | HYDR-019 | ACCESS PANEL: waterless trap | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ELPR-006 | RCD: residual current device | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ITIN-070 | OUTLET: MATV | 1 | to patient entertainment system, may be replaced with data outlet depending on ICT policy
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to patient entertainment system
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | HYDR-004 | DRAIN: floor waste | 1 | in case of spills, to be consolidated between multiple bays
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | LIFX-011 | LIGHT: reading light | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ELBO-015 | SWITCH: light, single | 1 | optional
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | MGAS-062 | OUTLET: suction, on services panel | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button and reading light switch on handset
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | low level, to recliner
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ELGP-222 | GPO: emergency power, double, on services panel | 3