## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | 9 | 24 Hours | 1 patient; 1 staff |  |  | A Patient Bed Bay used for the recovery of patients from anaesthetic, located within the Operating Unit or Day Procedures Unit. A clinical handwashing basin will be provided for each 4 Recovery Bed Bays. Recovery Bed Bays will require direct observation from the Staff Station.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to external window/s | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | DWWH-005 | WINDOW | 1 | Desirable | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | exam light | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELGP-105 | GPO: single, on services panel | 3 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | may serve a group of beds | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | for monitor, if required | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELGP-206 | GPO: double, on services panel, RCD protected | 1 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIHR-011 | BRACKET: for monitor | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIHR-019 | BRACKET: for suction bottle | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1 | optional | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIJO-194 | SHELF: laminate | 1 | to bedhead, full length | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIRT-023 | TRACK: curtain, bedscreen, L shaped | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FQGE-009 | CURTAIN: bed screen | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 2 | to louvred panel, if provided | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, call button on the handset | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, if networked monitoring required, with associated cabling; verify outlet type/s with monitor selected | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITIN-070 | OUTLET: MATV | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1 |  | Yes | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MGFP-002 | FLOWMETER: medical air | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MGFP-004 | FLOWMETER: oxygen | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMBE-014 | BED: patient, ICU, electric with mattress | 1 |  | Yes | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMGE-002 | ADAPTER: suction | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMGE-100 | SUCTION BOTTLE | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMHA-008 | MONITOR: patient, cardiac with vital signs | 1 | on bracket | Yes | Yes | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No