## Room Data
Standard Components - Room Data Sheet
Date of issue: 26.04.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | 12 | 8am to 8pm, daily | Up to 2 Staff |  |  | The Preparation Room provides a dedicated area for the extemporaneous preparation and compounding of non-aseptically prepared products and cleaning of equipment as required. The Preparation Room should be located in close proximity to the dispensing area.

## Items
Standard Components - Items in room
Date of issue: 26.04.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent to extend under basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 11
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 6
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 4
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-020 | BENCH: 600D, open under, laminate finish | 1 | may be height adjustable item depending on service requirements
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-141 | CUPBOARD: underbench, single door, adj shelves, lockable | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 3
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-148 | CUPBOARD: wall mount, double door, glazed, adj shelves, lockable | 3
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-159 | CUPBOARD: wall mount, single door, glazed, adj shelves, lockable | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FQSM-016 | TROLLEY | 1 | optional
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FQCW-019 | BIN: waste, general, 50L | 1 | quantity and type of bins to be based on local waste management policies
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | HYBA-010 | BASIN: handwash, Type B | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | HYBA-069 | SINK: single, with drainer, 930mmL | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | MEEX-013 | FUME CUPBOARD | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 2
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-212 | BULKHEAD: joinery | 2
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | MMGE-185 | SCALES: digital, benchtop | 2
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FQCW-065 | BIN: waste, pharmaceutical 50L | 1 | quantity and type of bins to be based on local waste management policies
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | SE | LIFX-008 | LIGHT: task light, built in | 2 | under wall mounted joinery
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 2 x task lights
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | SE | ELGP-208 | GPO: double, wall mounted | 4 | provision of emergency power to be determined based on service requirements