## Room Data
Standard Components - Room Data Sheet
Date of issue: 26.04.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PLNT-WT | Plant - Water Treatment | 18 | 24 Hours | 1 - 2 staff |  | High level sound isolation | The Plant - Water Treatment is a lockable room for water treatment systems, including particle filters, water softeners, carbon filters and reverse osmosis (RO) water plant/systems, for the provision of safe water for patients receiving haemodialysis therapy. The Water Treatment Plant Room should be located in close proximity to the Renal Dialysis Unit to permit short tubing runs to each Treatment Bay, and permit staff to monitor and service the water treatment systems. Refer to manufacturer's specifications for details of RO water treatment plant equipment. In particular, this equipment will incorporate a heat disinfection function, and water saving features. The final components of the system will be determined by the quality of feed water and the ability of the overall system to produce and maintain appropriate water quality. Water treatment requirements to be confirmed by a dialysis water treatment specialist. Special Design Requirements: High level sound isolation is required to ensure noise generated from this room does not invade treatment spaces. Structural engineer's assessment must be sought for floor load bearing capacity with respect to water treatment and pre-treatment plant equipment. Ventilation, exhaust and/or air-conditioning must be designed to accommodate the heat loads of the specified equipment. Light is to be minimised; there are to be no windows provided. Service access will be required around the perimeter of plant equipment, clearances will be determined by manufacturer's specifications. A second door may be provided for separate deliveries and maintenance access if located in the patient treatment area. Pipework and components installed after the water inlet in this room shall not contain brass or copper. Options for cooling of high temperature (circa 90°C) waste water discharged from RO plant is to be considered. Where chilled water is not available, a chiller may be required outside the plant room. The maximum temperature of the feed water to be assessed to allow determination of any requirement for a heat exchanger or chiller design as determined by expert. The intent of this is ensure the temperature at the dialysis point for patient care is between 30-37°C. Redundancy within the pre-treatment and treatment devices/filters should be considered based on the hospitals service criticality level, the feed water quality or risk around quality, and the hospital location where supply of replacement equipment is difficult.

## Items
Standard Components - Items in room
Date of issue: 26.04.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
PLNT-WT | Plant - Water Treatment | FA | FLGE-003 | FLOOR FINISH: concrete, sealed, trowel | 1
PLNT-WT | Plant - Water Treatment | FA | FLSK-002 | SKIRTING: concrete, coved to 150 AFFL, sealed | 6
PLNT-WT | Plant - Water Treatment | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
PLNT-WT | Plant - Water Treatment | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4
PLNT-WT | Plant - Water Treatment | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PLNT-WT | Plant - Water Treatment | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
PLNT-WT | Plant - Water Treatment | FA | DWSC-027 | DOOR: 1600mm c/o, 1 1/2 leaf, solid core, paint | 1 | lockable
PLNT-WT | Plant - Water Treatment | FA | DWSC-027 | DOOR: 1600mm c/o, 1 1/2 leaf, solid core, paint | 1 | optional secondary access door, lockable
PLNT-WT | Plant - Water Treatment | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PLNT-WT | Plant - Water Treatment | FFE | FQBS-051 | STOOL: mobile, adj height | 1 | optional
PLNT-WT | Plant - Water Treatment | FFE | MEGE-010 | HEAT EXCHANGER: supplied by mechanical chilled water | 1 | as required; may be necessary to cool feed water where high temperatures are expected, refer to technical expert for required outlet temperature (generally <25°C)
PLNT-WT | Plant - Water Treatment | FFE | HYGE-016 | PUMP: pressure booster | 2 | to suit water pressure drop through pre-filtration train where building water pressure and flow is inadequate
PLNT-WT | Plant - Water Treatment | FFE | HYGE-012 | WATER TREATMENT: reverse osmosis plant | 1 | details according to manufacturer's specifications
PLNT-WT | Plant - Water Treatment | FFE | FQSN-138 | PALLET: half size | 1
PLNT-WT | Plant - Water Treatment | FFE | HYGE-027 | DEVICE: UV irradiator | 1
PLNT-WT | Plant - Water Treatment | FFE | FQDW-051 | DESK: adj height, 1500W x 600D x 900H nom. | 1 | optional
PLNT-WT | Plant - Water Treatment | SE | ITBU-002 | ALARM: equipment monitoring, water treatment malfunction | 1 | connected to BMS and staff station in unit
PLNT-WT | Plant - Water Treatment | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
PLNT-WT | Plant - Water Treatment | SE | HYTP-008 | OUTLET: cold water | 1
PLNT-WT | Plant - Water Treatment | SE | HYDR-004 | DRAIN: floor waste | 1 | floor waste must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLNT-WT | Plant - Water Treatment | SE | HYDR-006 | DRAIN: tundish | 2
PLNT-WT | Plant - Water Treatment | SE | ELBO-015 | SWITCH: light, single | 1
PLNT-WT | Plant - Water Treatment | SE | ELBO-010 | SWITCH: light, 2-way | 1 | optional
PLNT-WT | Plant - Water Treatment | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 8 | for water treatment equipment, high level (power tools to be on a separate circuit)
PLNT-WT | Plant - Water Treatment | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | optional, dependent on equipment
PLNT-WT | Plant - Water Treatment | SE | HYGE-020 | WATER TREATMENT: carbon filter | 3 | 1 is optional; size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYGE-019 | WATER TREATMENT: brine tank | 1 | size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYGE-024 | WATER TREATMENT: softener tank | 1 | size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYGE-021 | WATER TREATMENT: multimedia tank | 1 | size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYGE-023 | WATER TREATMENT: particle filter, 5 microns | 1 | size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYGE-022 | WATER TREATMENT: particle filter, 1 micron | 1 | size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYDR-017 | DRAIN: floor waste, 300 x 300 | 1 | floor waste must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLNT-WT | Plant - Water Treatment | SE | ITBU-024 | ALARM: chlorine meter | 1 | optional, dependent on local operational policies
PLNT-WT | Plant - Water Treatment | SE | HYGE-028 | DEVICE: backflow prevention | 1
PLNT-WT | Plant - Water Treatment | SE | HYDR-018 | DRAIN: tundish, floor drain | 1 | tundish must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant