## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
PROC-20 | Procedure Room, 20m2 | 20 |  | 1 patient; 2-4 staff | 24 Hours | Sound attenuation level medium, Acoustic privacy is required. | The Procedure Room may be required for the performance of procedures that do not require the full facilities of the Operating Suite. This may include suturing or wounds, dressings, administration of local anaesthesia and use of medical gases in connection with the procedures being performed. General anaesthesia will not be administered in this room. Cardiac Protected electrical area Acoustics: Sound attenuation level - Medium. Acoustic privacy required. Additional Design Considerations: - Lead shielding may be required depending on use of Imaging equipment

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
PROC-20 | Procedure Room, 20m2 | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 1020 | Floor finish | 1 | Under basin. Significant change in colour to be avoided. | Vinyl, non-slip | Safety | Seamless, coved | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 2692 | Wall protection | 1 | or similar |  |  | Bed protection wall panel | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 2727 | Wall finish | 1 | Selection of material to comply with Part D Infection Prevention and Control AusHFG. |  |  | Splashback | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 5007 | Ceiling - Plasterboard | 1 | Between above bench joinery and ceiling. | Plasterboard | Paint | Bulkhead | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 5010 | Ceiling - Plasterboard | 1 |  | Plasterboard | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 6021 | Cornice | 1 |  | Tape set | Paint | Set between plasterboard wall and ceiling | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 8010 | Door protection | 1 |  | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 8040 | Door protection | 1 | Optional. To be decided at project level. | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | Fabrics | 9128 | Door - 1200mm | 1 | 1500mm clear opening, cover to glazing | Solid Core/ Glass | Paint | 1 1/2 leaf, observation panel | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FE | FE-11400 | Computer - PC & monitor | 1 | On bench or wall mounted, optional. If wall mounted add bracket. PACS images may be viewed, refer specific project requirements. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FE | FE-3100 | Basin - scrub, Type A | 1 | elbow action levers or handsfree optional. |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
PROC-20 | Procedure Room, 20m2 | FE | FE-36055 | Monitor - cardiac with vital signs | 1 | optional |  |  |  | Yes | Yes | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FE | FE-54520 | Telephone - handset, handsfree | 1 | to bench or wall mounted |  |  |  | No | Yes | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FE | FE-5622 | Bed - inpatient, electric + standard patient mattress | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FE | FE-5857 | Light - procedures small, ceiling | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FE | FE-9700 | Clock - analogue, electric | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-1050 | Bench - laminate | 1 | Optional . Length to suit layout, refer RLS or project specific requirements. |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-1465 | Bracket - suction bottle | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-1470 | Bracket - sharps | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-150 | Air flowmeter | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-15100 | Bracket - monitor | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-16250 | Oxygen flowmeter | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-19700 | Sharps bin | 1 | wall mounted |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-21700 | Stool - adjustable, mobile, high | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-21950 | Suction adapter | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-22000 | Suction bottle | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-4360 | Cupboard - door ht adj. shelves | 1 | Optional, lockable. Number to suit layout. |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-4420 | Cupboard - under bench, lockable | 2 | adjustable shelf, optional. Number to suit layout, refer RLS or project specific requirements. Storage solution for consumables and equipment to meet project specific Infection Control and WH&S requirements. |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-4470 | Cupboard - wall mounted, lockable | 2 | over bench, adjustable shelf, optional. Number to suit layout, refer RLS or project specific requirements. Storage solution for consumables and equipment to meet project specific Infection Control and WH&S requirements. |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-4600 | Curtain track - bed screen | 1 | to door opening |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-5000 | Curtain - bed screen | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-5550 | Blind - integral | 1 | Optional, to external windows. Number to suit window configuration. |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-5830 | Dispenser - antiseptic hand rub | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-6153 | Dispenser - moisturiser | 1 | Optional. Depends on Operational Policy. |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-6156 | Dispenser - soap | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | FF | FF-6214 | Trolley - equipment | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-10005 | Duress alarm | 1 | optional in ambulatory care area |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-1006 | Voice / Data outlet: double | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-11000 | Wall panel | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-1120 | Monitor connection facilities and cabling | 0 | May be replaced with data outlet, in accordance with ICT policy |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-6200 | Light switches | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-7000 | Oxygen (O2) | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-7010 | Nitrous Oxide (N2O) | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-7020 | Medical Air (MA) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-7040 | Suction | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-7070 | Scavenge | 1 | if N20 required |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-8000 | Patient/ Staff call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-8005 | Patient call handset | 1 | call button on the handset |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-9000 | GPO: Single | 3 | services panel |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-9000 | GPO: Single | 1 | low level for optional bed or exam couch |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-9001 | GPO: Double | 3 | to bench, computer PC + spare. |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-9010 | GPO: Emergency power, single (V) | 4 | services panel, 1 for monitor |  |  |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No