## Room Data
Standard Components - Room Data Sheet
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PROC | Procedure Room | 20 | 24 Hours | 1 patient; 2-4 staff |  | Sound attenuation level - High. Acoustic privacy is required. | The Procedure Room provides a controlled environment and facilities for carrying out procedures that do not require the full facilities of the Operating Suite. This may include suturing of wounds, complex dressings, lumbar puncture, catheterisations, administration of local anaesthesia and use of medical gases in connection with the procedures being performed. General anaesthesia will not be administered in this room. Additional Design Considerations: Lead shielding may be required depending on use of mobile imaging equipment. Treatment of bariatric patients including mobile, bariatric lifter access. The ceiling height has been nominally shown at 3000mm, however 2700mm is also acceptable and the height is to be determined based on ceiling mounted equipment and operational requirements.

## Items
Standard Components - Items in room
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
PROC | Procedure Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
PROC | Procedure Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
PROC | Procedure Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
PROC | Procedure Room | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
PROC | Procedure Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PROC | Procedure Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 4
PROC | Procedure Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PROC | Procedure Room | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 2
PROC | Procedure Room | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
PROC | Procedure Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PROC | Procedure Room | FFE | MGFP-002 | FLOWMETER: medical air | 1
PROC | Procedure Room | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | quantity to suit number of suction outlets
PROC | Procedure Room | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PROC | Procedure Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PROC | Procedure Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
PROC | Procedure Room | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
PROC | Procedure Room | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
PROC | Procedure Room | FFE | FQGE-010 | CURTAIN: privacy screen | 1
PROC | Procedure Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
PROC | Procedure Room | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
PROC | Procedure Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
PROC | Procedure Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
PROC | Procedure Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
PROC | Procedure Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
PROC | Procedure Room | FFE | MMGE-119 | TROLLEY: equipment | 1
PROC | Procedure Room | FFE | MMBE-043 | TROLLEY: patient, examination | 1
PROC | Procedure Room | FFE | FIHR-011 | BRACKET: for monitor, wall mounted | 1 | optional, for cardiac/vital signs monitor
PROC | Procedure Room | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | quantity to suit number of oxygen outlets
PROC | Procedure Room | FFE | MMMA-011 | MIXER: oxygen and nitrous oxide | 1 | optional, may be mobile, on trolley or wall mounted
PROC | Procedure Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
PROC | Procedure Room | FFE | FQBS-052 | STOOL: mobile, high, adj height | 1
PROC | Procedure Room | FFE | MMGE-002 | ADAPTER: suction | 2 | quantity to suit number of suction outlets
PROC | Procedure Room | FFE | MMGE-100 | SUCTION BOTTLE | 2 | quantity to suit number of suction outlets
PROC | Procedure Room | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
PROC | Procedure Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
PROC | Procedure Room | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
PROC | Procedure Room | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
PROC | Procedure Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
PROC | Procedure Room | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1 | optional, may be portable/mobile on stand
PROC | Procedure Room | FFE | MMHA-008 | MONITOR: patient, cardiac with vital signs | 1 | optional
PROC | Procedure Room | FFE | ITNE-023 | PRINTER: networked | 1 | optional
PROC | Procedure Room | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
PROC | Procedure Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
PROC | Procedure Room | FFE | FQCW-008 | BIN: waste, clinical, 50L | 1 | optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
PROC | Procedure Room | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
PROC | Procedure Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
PROC | Procedure Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 to telephone, 1 - optional, for cardiac/vital signs monitor
PROC | Procedure Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2
PROC | Procedure Room | SE | ELPR-006 | RCD: residual current device | 4
PROC | Procedure Room | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to procedure light
PROC | Procedure Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
PROC | Procedure Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional, dependent on service requirements, provide if nitrous oxide required
PROC | Procedure Room | SE | LIFX-008 | LIGHT: task light, built in | 1
PROC | Procedure Room | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 1 x task light, 1 x examination light
PROC | Procedure Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 is optional, quantity dependent on service requirements
PROC | Procedure Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional, dependent on service requirements
PROC | Procedure Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PROC | Procedure Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 is optional, quantity dependent on service requirements
PROC | Procedure Room | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light
PROC | Procedure Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset
PROC | Procedure Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
PROC | Procedure Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level, for patient trolley
PROC | Procedure Room | SE | ELGP-208 | GPO: double, wall mounted | 2
PROC | Procedure Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
PROC | Procedure Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | optional, for cardiac/vital signs monitor
PROC | Procedure Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
PROC | Procedure Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
PROC | Procedure Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PROC | Procedure Room | SE | ELGP-105 | GPO: single, on services panel | 3
PROC | Procedure Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3