## Room Template Data
Patient Bay - Emergency, Non Acute Treatment (PTB-E-NAC) - Room Template Properties and Room Template Data
2025-08-18
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | 10 | PBTR-NA | 6 | 18.08.2025 | 24 hours | 0 |  |  |  |  | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Non Acute Treatment provides the space and facilities for assessment, treatment and observation of patients with non acute conditions and injuries requiring a short episode of care (less than 24 hours) within the Emergency Unit. | ~ Clear line of sight to the patient in the patient bay from a staff station is required for patient observation. The patient bay may be configured with side walls. Inclusion, height and extent of side walls is to be determined at project level to suit the overall department layout and requirements for patient observation. ~ A handwash basin is to be provided for every four to six patient bays subject to the overall department layout and ease of access from each patient bay. Close access to a PPE bay shared between patient bays is required. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Inclusion of a patient monitor is optional, and provision is dependent on clinical services requirements. If provided, the location of the patient monitor is to be determined to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the monitor bracket. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. ~ The clear area required for patient transfer aids such as mobile hoists, patient slides and hover mats, and the staff required to assist the patient transfer, are to be considered for assisted patient transfers to and from beds. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ Provision for the temporary storage of patient property (e.g. wall-mounted baskets, coat hooks, etc.) should be considered for patient and visitor comfort and convenience. ~ Size, type and quantity of waste bins within a patient bay, including sharps, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. Waste bins and sharps bins may be provided in an area shared between multiple patient bays. ~ A dedicated power outlet, clearly separate from the Medical Services Panel (MSP), is recommended to support patient and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department, and they are to be spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable, and patient privacy must be considered when determining window placement. Where high-level windows are provided to the bedhead wall of patient bays consideration must be given to the location of wall mounted items such as patient monitors and to IPC requirements for window coverings. | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-08-18
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FIHR-110 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | for the temporary storage of patient property
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 1 | 1 |  | PES configuration will be dependent on operational models and local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | optional; required if patient monitor is provided; with cable and accessory management items as required
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | for the temporary storage of patient property
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | PES configuration will be dependent on operational models and local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of equipment to be confirmed to suit clinical services requirements; may alternatively be provided on a mobile stand to be shared across the unit and brought to the patient bay as required
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | optional; provision and configuration of monitoring to be confirmed to suit clinical services requirements
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | optional; may be provided in PPE bay shared between multiple bays
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | provide if patient bay is configured with side walls
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | FIN | WLPR-006.04 | WALL PROTECTION: corner guards, to 1500 AFFL | 1 | 1 | Wall Finish 3 | provide if patient bay is configured with side walls; to be coordinated with adjacent wall protection
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to recessed examination light
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to patient entertainment system
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional; to patient monitor if provided
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use/charging of portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | low height, for patient bed and mattress
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | placement to support quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; to patient monitor if provided
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | to patient entertainment system; may be replaced with a data outlet or alternate AV outlet depending on system requirements and local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to patient entertainment system
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; light may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | with control to patient handset
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of bed; placement to ensure visibility along paths of travel
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
Emergency | PTB-E-ACU
Emergency | PTB-E-ACU-E
Emergency | PTB-E-AMB
Emergency | PTB-E-AMT
Emergency | PTB-E-NAC
Emergency | TRIAGE-CO
Emergency | TRIAGE-RM
Emergency - PENDING PUBLICATION | CONS-ENT-OP
Emergency - PENDING PUBLICATION | PTB-E-RES
Emergency - PENDING PUBLICATION | RECP-E
Emergency - PENDING PUBLICATION | SSTN-E