## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
SCRB-8 | Scrub Up / Gowning, 8m2 | 8 | 24 Hours | Up to 3 |  | Sound attenuation level medium, Acoustic privacy is required. | The Scrub-up Gowning room provides an enclosed area for pre-operative scrubbing and gowning/ gloving. Additional Design Considerations: A minimum of 800mm is required between scrub stations. Taps to be non touch - automatically operated or foot operated.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | 910mm clear opening to Operating Rooms, entry door optional | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | to Operating Room, optional | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | DWOB-010 | OBSERVATION: through door/s, glass, clear | 1 | with cover, (sliding) | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to internal windows if provided | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | SE | ELGP-109 | GPO: single, wall mounted | 1 | for clock | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | FIBM-007 | MIRROR: fixed, glass, full length | 1 |  | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | FIDI-028 | DISPENSER: scrub brush | 3 |  | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 3 |  | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | FIJO-194 | SHELF: laminate | 1 | over trolleys | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | FIJO-200 | SHELF: stainless steel, over scrub sink, wall mount | 1 | over scrub trough | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1 | to wet zone | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | HYBA-077 | SINK: trough, scrub | 1 | auto/knee operated taps x 3 | No | No | Yes | No | Yes | Yes | Yes | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | HYTP-042 | TAPWARE: sensor | 3 |  | No | No | Yes | No | Yes | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | ITCL-014 | CLOCK: analogue, electric | 1 |  | Yes | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1 |  | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FFE | MMGE-122 | TROLLEY: gowns | 1 | optional | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 1 | As required, equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | WLWA-005 | WALL FINISH: paint, scrub resistant | 1 |  | No | No | No | No | No | No | No | No | No
SCRB-8 | Scrub Up / Gowning, 8m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 |  | No | No | No | No | No | No | No | No | No