## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
SECL | Seclusion Room | 15 | 24 Hours | 1 patient; 1-2 staff intermittently |  | Sound attenuation level high, Acoustic privacy is required. | A Seclusion Room provides for the sole confinement of a distressed or agitated person requiring separation for short periods at any hour of the day or night on an involuntary basis. The Seclusion Room will be observable from the Staff Station. An external outlook is desirable. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a standard nominal thickness of 10.38mm, or equivalent approved. Door and joinery hardware should not provide ligature points. Additional Design Considerations: - An internal observation window is required; a second room egress door is required

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
SECL | Seclusion Room | FA | CLCN-006 | CORNICE: plasterboard, 90mm to match ceiling finish, paint | 1 |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | 3000 mm height | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | DWGL-025 | DOOR: 1100mm c/o, single leaf, observation panel, solid core/ safety glass, paint | 1 | 1100mm clear opening, lockable from outside; anti-ligature door hardware. 2 no. required unless 500 c/o door | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | DWGL-073 | DOOR: 500mm c/o, single leaf, observation panel, solid core/safety glass, paint | 1 | 500mm clear outward opening, optional where preferred second door not possible, anti-ligature door hardware | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | DWOB-006 | OBSERVATION: internal window, alum/safety glass, double glazed, integral venetian blind, powdercoat | 1 | Optional, Grade A safety glass | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | DWOB-013 | OBSERVATION: through door/s, safety glass, double glazed with integral venetian blind, powdercoat | 2 | Grade A safety glass | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to windows & doors, controls outside room | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | DWWH-005 | WINDOW | 1 | external windows double glazed Grade A safety glass with integral venetians | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for CCTV camera | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | FLVY-002 | FLOOR FINISH: vinyl, seamless, coved, cushioned | 1 |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FFE | FQBS-047 | MATTRESS: foam | 1 | foam, on floor | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FFE | ITSE-013 | CAMERA: CCTV, indoor, fixed dome | 1 | tamper proof | Yes | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | LIFX-001 | LIGHT: night light, tamper proof | 1 | high level, dimmable | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | LIFX-010 | LIGHT: reading light, tamper proof | 1 | sealed, dimmable | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | WLWA-017 | WALL FINISH: vinyl, cushioned, full height | 1 |  | No | No | No | No | No | No | No | No | No