## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
AMBTR | Ambulance Triage | 12 |  | Up to 3 | 24 Hours |  | The Ambulance Triage is an area for receipt and assessment of patients arriving in the Unit by ambulance. The Ambulance Triage will be adjacent to the Ambulance entry which should include an Airlock.
SHDEC | Shower - Decontamination | 8 |  | 1 - 2 | 24 Hours |  | The Decontamination Shower is provided to shower patients who arrive in the Unit contaminated with toxic and/or infectious substances. The room will include a flexible water hose, floor drain and contaminated water trap. The shower should be accessible from the ambulance bay without entering any other part of the Unit. A Personal Protective Equipment Bay may be located in close proximity.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
SHDEC | Shower - Decontamination | Fabrics | 1025 | Floor finish | 1 | tiles also acceptable | Vinyl, non slip | Studded | Seamless, coved | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | Fabrics | 2000 | Skirting | 1 | or tiles for tiled floor | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | Fabrics | 3070 | Wall finish | 1 | to wet areas; tiles also acceptable | Vinyl | Prefinished | Wall vinyl full height | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | Fabrics | 5023 | Ceiling - Plasterboard | 1 |  | Plasterboard | Prefinished | Water resistant, drop in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | Fabrics | 8010 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | Fabrics | 8040 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | Fabrics | 9001 | Door - 1100mm | 1 | 910mm clear; Outward opening; privacy latch; emergency release. | Solid Core | Paint | Single leaf | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | FE | FE-47605 | Shower - decontamination | 1 | in lockable cabinet |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
SHDEC | Shower - Decontamination | FF | FF-6152 | Dispenser - disposable glove | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | SE | S-11000 | Wall panel | 1 | recessed, lockable cover, if gases required |  |  |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | SE | S-4030 | Drainage | 1 | to contaminated water trap |  |  |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | SE | S-5015 | Ventilation | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | SE | S-5019 | Exhaust | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | SE | S-6200 | Light switches | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | SE | S-7000 | Oxygen (O2) | 1 | in lockable recess, optional |  |  |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | SE | S-7020 | Medical Air (MA) | 1 | in lockable recess, optional |  |  |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | SE | S-7040 | Suction | 1 | in lockable recess, optional |  |  |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination | SE | S-8080 | Emergency call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No