## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
SHDEC | Shower - Decontamination, 8m2 | 8 | 24 Hours | 1 - 2 |  |  | The Decontamination Shower is provided to shower patients who arrive in the Unit contaminated with toxic and/or infectious substances. The room will include a flexible water hose, floor drain and contaminated water trap. The shower should be accessible from the ambulance bay without entering any other part of the Unit. A Personal Protective Equipment Bay may be located in close proximity.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
SHDEC | Shower - Decontamination, 8m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | equal to Acrovyn | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | equal to Acrovyn | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | outward opening; privacy latch; emergency release; no. of doors to suit layout | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | SE | ELBO-015 | SWITCH: light, single | 2 |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 2 |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for tiled floor | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | FA | FLVY-005 | FLOOR FINISH: vinyl, seamless, coved, non slip, studded | 1 | tiles also acceptable | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | SE | HYDR-001 | DRAIN: special requirements | 1 | to contaminated water trap | No | No | No | No | No | No | Yes | No | No
SHDEC | Shower - Decontamination, 8m2 | FFE | HYTP-017 | SHOWER: decontamination | 1 | in lockable cabinet | No | No | Yes | No | Yes | Yes | Yes | No | No
SHDEC | Shower - Decontamination, 8m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | SE | MGAS-023 | OUTLET: medical air (MA), wall mounted | 1 | in lockable recess, optional | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | SE | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 | in lockable recess, optional | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | SE | MGAS-063 | OUTLET: suction, wall mounted | 1 | in lockable recess, optional | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | FFE | MMBE-025 | GURNEY | 1 |  | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | recessed, lockable cover, if gases required | No | No | No | No | No | No | No | No | No
SHDEC | Shower - Decontamination, 8m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable | No | No | No | No | No | No | No | No | No