## Room Template Data
Staff Station - Emergency, Control Hub (SSTN-E) - Room Template Properties and Room Template Data
2025-08-18
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
SSTN-E | Staff Station - Emergency, Control Hub | 14 |  | 1 | 18.08.2025 | 24 hours | 0 |  |  |  |  | 3 staff, with 1-2 additional staff intermittently | The Staff Station - Emergency, Control Hub provides the space and facilities for a central operational and administrative base of an Emergency Department. It supports the coordination of patient care, patient flow, and ambulance arrivals as well as overseeing central monitoring, security feeds and ambulance phone. These functions may be distributed across the unit depending on operational models, staffing profile, size and complexity of service, etc. | ~ This Standard Component indicates 3 x workstations (providing a base for 1 x doctor-in-charge, 1 x nurse-in-charge and 1 x clerk), with an additional area for central monitoring. The number of workstations required will vary depending on operational models, staffing models and size and complexity of service. The minimum recommended size of a workstation bench space is 1200mm wide x 700mm deep. ~ One computer workstation has been shown as a downtime workstation with provision of UPS power. Requirements for and location of downtime facilities will need to be confirmed to meet clinical service requirements, operational models for downtime, and local ICT policies. Provision of downtime computers will need to be rationalised across the unit to avoid unnecessary duplication (e.g. if a Clinical Workroom and/or multiple Staff Stations with tentative downtime allocations are provided). ~ The Staff Station - Emergency, Control Hub may be enclosed (e.g. with security glazing and lockable doors) or other physical design/planning solutions may be considered (e.g. increased counter depth, egress to secure area) for staff safety and security. Requirements are to be determined at project level based on a risk assessment. If provided, security glazing configuration (size of communication slot, size of pass-through aperture for samples/paperwork, etc.) is to be determined at project level to suit clinical service requirements and operational models. Provision of a Hearing Loop and associated items (microphones, signage, etc.) may also be required to suit the configuration of the counter and security glazing. ~ The quantity and type of display screens required to oversee and control the flow of patients throughout the Emergency Department (including ambulance arrivals, emergency patient flow and security feeds) are to be confirmed at project level to suit clinical service requirements and operational models. ~ If overall department planning results in rooms being accessed from behind the Staff Station, additional area for appropriate door circulation clearances will be required. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and work health and safety (WHS) policies and operational service requirements. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Acoustic treatments may be considered to assist with noise transfer from adjacent spaces. All materials must meet local infection prevention and control (IPC) policies. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Placement and visibility of nurse annunciators in adjacent corridors must be considered and coordinated with other ceiling elements such as bulkheads. ~ The type, extent and configuration of storage within the room for stationery and consumables will be dependent on service requirements and operational models. This includes considering the facility’s use of electronic medical records (EMR) as well as remaining paper forms. ~ Size, type and quantity of waste bins will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ The requirement for Body Protection under AS/NZS 3003 is to be determined at project level depending on the proximity of the counter to adjacent patient areas. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Wall mounted fire services items may be included in the Staff Station or provided nearby in a conspicuous and readily accessible position including a mimic panel, warden intercom phone, manual call point, break glass alarm, portable fire extinguisher and fire blanket. A ceiling mounted visual alarm device may also be provided in the Staff Station or in an adjacent corridor. Inclusion of these items in the Staff Station will be dependent on the overall department layout. Location, mounting heights and clearances to meet AS1670.1 and AS2444. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-08-18
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
SSTN-E | Staff Station - Emergency, Control Hub | FFE | JORS-021 | JOINERY UNIT: staff station | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | FFE | FQBS-171 | CHAIR: office, ergonomic | 3 | 1
SSTN-E | Staff Station - Emergency, Control Hub | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 3 | 1
SSTN-E | Staff Station - Emergency, Control Hub | FFE | ITNE-071 | TELEPHONE: handset, desktop | 3 | 1 |  | 1 to each workstation
SSTN-E | Staff Station - Emergency, Control Hub | FFE | JOBE-251 | CAP: cable access | 4 | 1
SSTN-E | Staff Station - Emergency, Control Hub | FFE | ITNE-316 | PRINTER: labels, small, desktop | 2 | 1
SSTN-E | Staff Station - Emergency, Control Hub | FFE | FQSM-061 | PEDESTAL: mobile, 660H nominal, 2 equal drawers and 1 file drawer | 2 | 1
SSTN-E | Staff Station - Emergency, Control Hub | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | FFE | FQWS-212 | BIN: confidential document, secure, 30L | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | FFE | ITNE-302 | MULTIFUNCTION DEVICE: printer/copier/scanner/fax, floor standing | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | ambulance phone
SSTN-E | Staff Station - Emergency, Control Hub | FFE | ITSE-111 | DISPLAY SCREEN: security, CCTV monitoring | 1 | 1 |  | type and size of screen to be confirmed to suit security requirements
SSTN-E | Staff Station - Emergency, Control Hub | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 3 |  | optional; for ambulance arrivals information; provision dependent on operational models and clinical service requirements
SSTN-E | Staff Station - Emergency, Control Hub | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 3 |  | optional; for emergency department patient flow information; provision dependent on operational models and clinical service requirements
SSTN-E | Staff Station - Emergency, Control Hub | FFE | JORS-071 | SECURITY GLAZING: to staff station | 3 | 1 |  | optional; provision to be determined at project level based on risk assessment; may include communication slots and pass through apertures; final configuration to be confirmed at project level to suit clinical service requirements and operational models.
SSTN-E | Staff Station - Emergency, Control Hub | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | optional; provide if display screen for ambulance arrivals information is provided
SSTN-E | Staff Station - Emergency, Control Hub | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | optional; provide if display screen for patient flow information is provided
SSTN-E | Staff Station - Emergency, Control Hub | FFE | FIBM-021 | WHITEBOARD: fixed, magnetic, integral to joinery | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | FFE | FIHR-333 | BRACKET: television/AV system display screen, single, fixed, ceiling mounted | 1 | 1 |  | to security CCTV display screen
SSTN-E | Staff Station - Emergency, Control Hub | FFE | MMPM-092 | MONITOR: central patient monitoring station, dual display screens | 1 | 1 |  | quantity and size of display screens to suit patient monitoring requirements
SSTN-E | Staff Station - Emergency, Control Hub | FFE | ITBU-470 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall mounted | 1 | 1 |  | type of clock and connection to the master clock system is to be confirmed at a project level based on clinical service requirements
SSTN-E | Staff Station - Emergency, Control Hub | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
SSTN-E | Staff Station - Emergency, Control Hub | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
SSTN-E | Staff Station - Emergency, Control Hub | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
SSTN-E | Staff Station - Emergency, Control Hub | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
SSTN-E | Staff Station - Emergency, Control Hub | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice
SSTN-E | Staff Station - Emergency, Control Hub | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | 1 | Wall Protection | to be coordinated with adjacent wall protection
SSTN-E | Staff Station - Emergency, Control Hub | SER | ITSE-063 | BUTTON: security, duress, fixed, under bench mounted | 2 | 1
SSTN-E | Staff Station - Emergency, Control Hub | SER | LIFX-108 | LIGHT: task, integral to joinery | 4 | 1 |  | 1 to each workstation, 1 to central patient monitoring station
SSTN-E | Staff Station - Emergency, Control Hub | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to multi-function device
SSTN-E | Staff Station - Emergency, Control Hub | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to security CCTV display screen
SSTN-E | Staff Station - Emergency, Control Hub | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 1 | 1 |  | to security CCTV display screen
SSTN-E | Staff Station - Emergency, Control Hub | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 4 | 1 |  | 1 to each workstation, 1 to central patient monitoring station
SSTN-E | Staff Station - Emergency, Control Hub | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | optional; provide if display screen for ambulance arrivals information is provided
SSTN-E | Staff Station - Emergency, Control Hub | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to clock; an additional power outlet may be required if power over ethernet (PoE) is not supported by the clock hardware
SSTN-E | Staff Station - Emergency, Control Hub | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to multi-function device
SSTN-E | Staff Station - Emergency, Control Hub | SER | ELSW-011 | SWITCH PLATE: light, multi-gang | 1 | 3 |  | optional; may be provided for control of general lighting in nearby areas; provision dependent on overall department layout
SSTN-E | Staff Station - Emergency, Control Hub | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | to task lighting
SSTN-E | Staff Station - Emergency, Control Hub | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | optional; provide if display screen for patient flow information is provided
SSTN-E | Staff Station - Emergency, Control Hub | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; provide if display screen for ambulance arrivals information is provided
SSTN-E | Staff Station - Emergency, Control Hub | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; provide if display screen for patient flow information is provided
SSTN-E | Staff Station - Emergency, Control Hub | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to ambulance phone
SSTN-E | Staff Station - Emergency, Control Hub | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 1 | 1 |  | 2 to each workstation (except downtime workstation), 2 to central patient monitoring station
SSTN-E | Staff Station - Emergency, Control Hub | SER | ELGP-271 | GPO: double, UPS, joinery mounted | 2 | 1 |  | to downtime computer workstation
SSTN-E | Staff Station - Emergency, Control Hub | SER | ELGP-211 | GPO: double, joinery mounted | 3 | 1 |  | 1 to each workstation; over bench for portable device charging
SSTN-E | Staff Station - Emergency, Control Hub | SER | ELGP-211 | GPO: double, joinery mounted | 2 | 1 |  | to label printers
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
Emergency | CONS-ENT-OP
Emergency | PTB-E-ACU
Emergency | PTB-E-ACU-E
Emergency | PTB-E-AMB
Emergency | PTB-E-AMT
Emergency | PTB-E-NAC
Emergency | PTB-E-RES
Emergency | RECP-E
Emergency | SSTN-E
Emergency | TRIAGE-CO
Emergency | TRIAGE-RM