## Room Template Data
Laundry - Mental Health (LAUN-MH) - Room Template Properties and Room Template Data
2025-08-20
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
LAUN-MH | Laundry - Mental Health | 6 |  | 5 | 20.08.2025 |  | 1 | 8am | 6pm | daily | (may vary depending on operational models) | 1 patient; 1 staff | The Laundry - Mental Health provides the space and facilities for consumers to wash and dry clothing while staying in the Mental Health unit. Consumer access to this room and level of staff supervision is to be confirmed at project level to suit service requirements. | ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings of a type manufactured and marketed as anti-ligature (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. Anti-ligature fittings may require a performance solution to be provided for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~All glazing is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ A second door may be required for safety and security; provision will be dependent on service requirements and local Work Health and Safety (WHS) policies. The location of the second door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ This Standard Component shows a bench, laundry sink, and a domestic washing machine and dryer. Ironing facilities are not included, and provision will be based on operational models. The use and storage of clothes airers/drying racks may be considered, and inclusion would be based on a risk assessment and operational models. ~ The selection of finishes in rooms for mental health units is to support provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate and institutional feel. ~ The number of washing machines and dryers required will vary depending on the size of the unit and the operational models for handling patient laundry. Additional space will be required to accommodate any increase in the number of machines. ~ While domestic washing machines and dryers are typically selected, the increased frequency of use compared to residential applications must be considered to ensure robustness and longevity of the selected items. ~ Air conditioning and exhaust requirements are to be confirmed to suit the number of machines and anticipated frequency of use. ~ A residual current device (RCD) has been shown within this room. Requirement for restricted access to RCDs as per AS/NZS 3003 is to be confirmed at project level. Where access needs to be restricted, RCDs may be consolidated in a staff area (e.g. at the staff station). ~ Anti-pick caulking is recommended for finishing between surfaces. | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-08-20
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
LAUN-MH | Laundry - Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
LAUN-MH | Laundry - Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | optional; provision dependent on frame material and finish
LAUN-MH | Laundry - Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 1 | requirements for glazing in vision panel to be confirmed to suit the mental health environment
LAUN-MH | Laundry - Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to both sides
LAUN-MH | Laundry - Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional; provision dependent on frame material and finish
LAUN-MH | Laundry - Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 3 | Internal - Door 2 | optional; secondary egress; provision dependent on local WHS policies; requirements for glazing in vision panel to be confirmed to suit the mental health environment
LAUN-MH | Laundry - Mental Health | D+W | WIFX-009.01 | WINDOW: fixed, internal, single glazed, sill at 1200H | 1 | 1 | Internal - Window 1 | requirements for glazing in vision panel to be confirmed to suit the mental health environment
LAUN-MH | Laundry - Mental Health | FFE | FQCL-101 | WASHING MACHINE: laundry, domestic, front loading | 1 | 1 |  | quantity to suit service requirements
LAUN-MH | Laundry - Mental Health | FFE | FQCL-111 | DRYER: laundry, domestic | 1 | 1 |  | quantity to suit service requirements
LAUN-MH | Laundry - Mental Health | FFE | FQCL-121 | PLINTH: washing machine, domestic | 1 | 1 |  | for improved reaching height to machine opening; as required to suit configuration and machines selected; washing machine may alternatively be floor standing
LAUN-MH | Laundry - Mental Health | FFE | FQCL-141 | STACKING KIT: washing machine and dryer, domestic | 1 | 1 |  | as required to suit configuration and machines selected; dryer may alternatively be on a plinth or floor standing
LAUN-MH | Laundry - Mental Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on service requirements, operational models for waste management and local IPC policies
LAUN-MH | Laundry - Mental Health | FFE | HYBA-411 | SINK: laundry, single bowl | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby fixtures
LAUN-MH | Laundry - Mental Health | FFE | HYTP-184 | TAPWARE: sink, tap set, wall mounted, anti-ligature | 1 | 1 |  | selection of sink and tapware should be coordinated to ensure compatibility
LAUN-MH | Laundry - Mental Health | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
LAUN-MH | Laundry - Mental Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 2 | 1 |  | lockable
LAUN-MH | Laundry - Mental Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | lockable
LAUN-MH | Laundry - Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
LAUN-MH | Laundry - Mental Health | FFE | JOSH-105 | SHELF UNIT: wall mounted, pigeonholes | 1 | 1
LAUN-MH | Laundry - Mental Health | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1
LAUN-MH | Laundry - Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting
LAUN-MH | Laundry - Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
LAUN-MH | Laundry - Mental Health | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2
LAUN-MH | Laundry - Mental Health | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
LAUN-MH | Laundry - Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
LAUN-MH | Laundry - Mental Health | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | 1 to washing machine; 1 to dryer
LAUN-MH | Laundry - Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1
LAUN-MH | Laundry - Mental Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
LAUN-MH | Laundry - Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1
LAUN-MH | Laundry - Mental Health | SER | HYDR-022 | DRAIN: floor waste, round, tamper proof, anti-ligature | 1 | 1
LAUN-MH | Laundry - Mental Health | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | to washing machine
LAUN-MH | Laundry - Mental Health | SER | HYTP-432 | OUTLET: water, hot | 1 | 1 |  | to washing machine
LAUN-MH | Laundry - Mental Health | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1
LAUN-MH | Laundry - Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink
LAUN-MH | Laundry - Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to sink
LAUN-MH | Laundry - Mental Health | SER | HYDR-201.01 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
Emergency | CONS-ENT-OP
Emergency | PTB-E-ACU
Emergency | PTB-E-ACU-E
Emergency | PTB-E-AMB
Emergency | PTB-E-AMT
Emergency | PTB-E-NAC
Emergency | PTB-E-RES
Emergency | RECP-E
Emergency | SSTN-E
Emergency | TRIAGE-CO
Emergency | TRIAGE-RM