## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
STRT | Stress Testing | 12 |  | 1 patient; 1 - 2 staff | Available 24 Hours | Acoustic privacy is required | Room for undertaking patient diagnostic stress testing procedures. The Stress Testing room should be located close to patient toilet and change rooms. Acoustics: Acoustic privacy required Body Protected electrical area

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Items | [6 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
STRT | Stress Testing | FE | FE-11400 | Computer - PC & monitor | 1 |  |  |  |  | Yes | Yes | No | No | No | No | No | No | No
STRT | Stress Testing | FE | FE-2800 | Basin - handwash, Type B | 1 | refer to BHWS-B (sim) |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
STRT | Stress Testing | FE | FE-54510 | Telephone - handset, standard | 1 | to computer table |  |  |  | No | Yes | No | No | No | No | No | No | No
STRT | Stress Testing | FE | FE-56600 | Treadmill - automatic | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-1650 | Chair - client | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-2100 | Chair - ergonomic, office | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-22615 | Table - computer | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-3350 | Clock - battery operated | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-3400 | Coathook | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-4700 | Curtain track - privacy screen (90 deg) | 1 | to entry door |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-5250 | Curtain - privacy screen | 1 | to entry door |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-6156 | Dispenser - soap | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-7520 | Exercise bicycle | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-9001 | GPO: Double | 4 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-9015 | GPO: Cleaner | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-1006 | Voice / Data outlet: double | 1 | 1 outlet for telephone |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-8000 | Patient/ Staff call | 2 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-8005 | Patient call handset | 2 | call button on the handset |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-8010 | Staff/ Nurse assist call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | Fabrics | 3060 | Wall finish | 1 | to basin; tiles also acceptable | Vinyl | Prefinished | Splashback | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | Fabrics | 5060 | Ceiling - Acoustic | 1 |  | Acoustic | Prefinished | Drop-in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | Fabrics | 8010 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | Fabrics | 8040 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | Fabrics | 9004 | Door - 1100mm | 1 | 910mm clear opening | Solid Core/ Glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
STRT | Stress Testing | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No