## Room Data
Standard Components - Room Data Sheet
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
TRMT | Treatment Room | 14 | 24 Hours | 1 patient; 1-2 staff |  | Sound attenuation level high, Acoustic privacy is required. | The Treatment Room provides a controlled environment, privacy and facilities for carrying out consultations, examinations, treatments and minor procedures.

## Items
Standard Components - Items in room
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
TRMT | Treatment Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
TRMT | Treatment Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
TRMT | Treatment Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
TRMT | Treatment Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
TRMT | Treatment Room | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
TRMT | Treatment Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
TRMT | Treatment Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 5
TRMT | Treatment Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
TRMT | Treatment Room | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
TRMT | Treatment Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
TRMT | Treatment Room | FFE | MGFP-002 | FLOWMETER: medical air | 1
TRMT | Treatment Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1
TRMT | Treatment Room | FFE | FIHR-016 | BRACKET: for sharps bin | 1
TRMT | Treatment Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
TRMT | Treatment Room | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
TRMT | Treatment Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
TRMT | Treatment Room | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
TRMT | Treatment Room | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
TRMT | Treatment Room | FFE | FQGE-010 | CURTAIN: privacy screen | 1
TRMT | Treatment Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
TRMT | Treatment Room | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
TRMT | Treatment Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
TRMT | Treatment Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
TRMT | Treatment Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
TRMT | Treatment Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
TRMT | Treatment Room | FFE | MMGE-119 | TROLLEY: equipment | 1
TRMT | Treatment Room | FFE | MMBE-043 | TROLLEY: patient, examination | 1
TRMT | Treatment Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1
TRMT | Treatment Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
TRMT | Treatment Room | FFE | FQBS-052 | STOOL: mobile, high, adj height | 1
TRMT | Treatment Room | FFE | MMGE-002 | ADAPTER: suction | 1
TRMT | Treatment Room | FFE | MMGE-100 | SUCTION BOTTLE | 1
TRMT | Treatment Room | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
TRMT | Treatment Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
TRMT | Treatment Room | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
TRMT | Treatment Room | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1 | optional, may be portable/mobile on stand
TRMT | Treatment Room | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
TRMT | Treatment Room | FFE | ITNE-023 | PRINTER: networked | 1 | optional
TRMT | Treatment Room | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
TRMT | Treatment Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
TRMT | Treatment Room | FFE | FQCW-008 | BIN: waste, clinical, 50L | 1 | optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
TRMT | Treatment Room | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
TRMT | Treatment Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
TRMT | Treatment Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to telephone
TRMT | Treatment Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2
TRMT | Treatment Room | SE | ELPR-006 | RCD: residual current device | 4
TRMT | Treatment Room | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to exam light
TRMT | Treatment Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light
TRMT | Treatment Room | SE | LIFX-008 | LIGHT: task light, built in | 1 | under wall mounted joinery
TRMT | Treatment Room | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 1 x task light, 1 x examination light
TRMT | Treatment Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
TRMT | Treatment Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
TRMT | Treatment Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1
TRMT | Treatment Room | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel + indicator button & light
TRMT | Treatment Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, call button on the handset
TRMT | Treatment Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
TRMT | Treatment Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level, for patient trolley
TRMT | Treatment Room | SE | ELGP-208 | GPO: double, wall mounted | 2
TRMT | Treatment Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
TRMT | Treatment Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
TRMT | Treatment Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
TRMT | Treatment Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
TRMT | Treatment Room | SE | ELGP-105 | GPO: single, on services panel | 3
TRMT | Treatment Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2