## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ULTR | Ultrasound Room | 14 | Available 24 Hours | 1 patient with up to 1 support person; 1-2 staff |  | Acoustic privacy is required | Room for diagnostic ultrasound imaging, located close to patient toilet and change rooms. The room will require access for patients on hospital beds.

## Items
Standard Components - Items in room
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
ULTR | Ultrasound Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
ULTR | Ultrasound Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
ULTR | Ultrasound Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
ULTR | Ultrasound Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
ULTR | Ultrasound Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
ULTR | Ultrasound Room | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin; selection of material to comply with AHFG Part D Infection Control
ULTR | Ultrasound Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiled ceiling also acceptable
ULTR | Ultrasound Room | FA | DWSC-012 | DOOR: 1200mm c/o, 1 1/2 leaf, solid core, paint | 1
ULTR | Ultrasound Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ULTR | Ultrasound Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 6
ULTR | Ultrasound Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
ULTR | Ultrasound Room | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1 | optional
ULTR | Ultrasound Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
ULTR | Ultrasound Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
ULTR | Ultrasound Room | FFE | FQSN-031 | CABINET: short, single door, tambour, adj shelves, lockable | 1
ULTR | Ultrasound Room | FFE | FIJO-157 | CUPBOARD: wall mount, single door, adj shelves, lockable | 1 | over mobile storage unit
ULTR | Ultrasound Room | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
ULTR | Ultrasound Room | FFE | FIRT-031 | TRACK: curtain, privacy | 1 | optional, external to entry doors
ULTR | Ultrasound Room | FFE | FQGE-010 | CURTAIN: privacy screen | 2 | 1-internal to entry door, 1-external to entry door optional
ULTR | Ultrasound Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
ULTR | Ultrasound Room | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
ULTR | Ultrasound Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1
ULTR | Ultrasound Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
ULTR | Ultrasound Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
ULTR | Ultrasound Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
ULTR | Ultrasound Room | FFE | MMBE-043 | TROLLEY: patient, examination | 1
ULTR | Ultrasound Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
ULTR | Ultrasound Room | FFE | FIHR-055 | RACK: scanhead | 1
ULTR | Ultrasound Room | FFE | FQBS-051 | STOOL: mobile, adj height | 1
ULTR | Ultrasound Room | FFE | FQSM-016 | TROLLEY | 1 | for gel warmer
ULTR | Ultrasound Room | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
ULTR | Ultrasound Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
ULTR | Ultrasound Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
ULTR | Ultrasound Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
ULTR | Ultrasound Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
ULTR | Ultrasound Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
ULTR | Ultrasound Room | FFE | MMMI-340 | DISPLAY SCREEN: slave, for ultrasound | 1
ULTR | Ultrasound Room | FFE | MMMI-329 | DEVICE: imaging, ultrasound scanning unit | 1
ULTR | Ultrasound Room | FFE | FQDW-028 | WORKSTATION: straight, adj height, 1200W x 750D x 750H nom. | 1
ULTR | Ultrasound Room | FFE | FIJO-212 | BULKHEAD: joinery | 1
ULTR | Ultrasound Room | FFE | MMGE-169 | SLING: arm, dynamic, ceiling mounted | 1
ULTR | Ultrasound Room | FFE | MMMI-376 | WARMER: gel | 1 | on trolley
ULTR | Ultrasound Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 2-scanning station; 1-desk
ULTR | Ultrasound Room | SE | ELPR-006 | RCD: residual current device | 2
ULTR | Ultrasound Room | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for slave display screen
ULTR | Ultrasound Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
ULTR | Ultrasound Room | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light
ULTR | Ultrasound Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset
ULTR | Ultrasound Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ULTR | Ultrasound Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | to patient bed
ULTR | Ultrasound Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | clock
ULTR | Ultrasound Room | SE | ELGP-208 | GPO: double, wall mounted | 2 | desk
ULTR | Ultrasound Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | scanning station
ULTR | Ultrasound Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | as required
ULTR | Ultrasound Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
ULTR | Ultrasound Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
ULTR | Ultrasound Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
ULTR | Ultrasound Room | SE | ITIN-061 | OUTLET: HDMI, ceiling mounted | 1
ULTR | Ultrasound Room | SE | ITIN-066 | OUTLET: HDMI, wall mounted | 1
ULTR | Ultrasound Room | SE | ELGP-105 | GPO: single, on services panel | 2
ULTR | Ultrasound Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2 | patient services panel