## Room Data
Standard Components - Room Data Sheet
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
WCPT | Toilet - Patient | 4 | 24 Hours | 1 patient; 1 staff assisting as required |  | Sound attenuation level high, Acoustic privacy is required. | The Toilet - Patient provides a toilet and basin for use by patients (with or without assistance). Emergency release door hardware should be installed to allow staff access in an emergency. The entrance to the room should be flush with the adjoining floor for access in commode chairs/wheelchairs. Signage with braille tactile nominating 'Unisex Patient WC' required

## Items
Standard Components - Items in room
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
WCPT | Toilet - Patient | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
WCPT | Toilet - Patient | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | tiles are also acceptable
WCPT | Toilet - Patient | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
WCPT | Toilet - Patient | FA | WLWA-007 | WALL FINISH: splashback | 1
WCPT | Toilet - Patient | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
WCPT | Toilet - Patient | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
WCPT | Toilet - Patient | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | with privacy latch, emergency release required if inward opening door
WCPT | Toilet - Patient | FA | CLCN-009 | CORNICE: wall trim fixing | 1
WCPT | Toilet - Patient | FFE | FIHR-026 | HOOK: coat | 2
WCPT | Toilet - Patient | FFE | FQCW-016 | BIN: waste, general, 20L | 1
WCPT | Toilet - Patient | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
WCPT | Toilet - Patient | FFE | FIDI-030 | DISPENSER: soap | 1
WCPT | Toilet - Patient | FFE | FIDI-036 | DISPENSER: toilet paper | 1
WCPT | Toilet - Patient | FFE | FIRT-006 | GRAB RAIL: WC | 1
WCPT | Toilet - Patient | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | optional
WCPT | Toilet - Patient | FFE | FIBM-006 | MIRROR: fixed, glass | 1
WCPT | Toilet - Patient | FFE | FQCW-037 | BIN: waste, sanitary | 1
WCPT | Toilet - Patient | FFE | HYBA-011 | BASIN: handwash, Type C | 1
WCPT | Toilet - Patient | FFE | HYWC-006 | TOILET SUITE: patient | 1
WCPT | Toilet - Patient | FFE | HYTP-035 | TAPWARE: mixer, basin, accessible | 1
WCPT | Toilet - Patient | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
WCPT | Toilet - Patient | SE | HYDR-004 | DRAIN: floor waste | 1
WCPT | Toilet - Patient | SE | ELBO-015 | SWITCH: light, single | 1
WCPT | Toilet - Patient | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light
WCPT | Toilet - Patient | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light