## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
WTPL | Water Treatment Plant Room | 15 | 24 Hours | 1 - 2 |  | High level sound isolation | The Water Treatment Plant Room is a lockable room for water treatment systems used in dialysis, including booster pumps, particle filters, water softeners, carbon filters and reverse osmosis systems. Refer to Manufacturer's Specifications for details of Reverse Osmosis (RO) Water Treatment Plant equipment. In particular this equipment will incorporate a heat disinfection function, and water saving features. The Water Treatment Plant Room should be located in close proximity to the Renal Dialysis Unit to permit short tubing runs to each Treatment Bay, and permit staff to monitor and service the water treatment systems. Special Design Requirements: Ventilation, exhaust and/or airconditioning must be deisgned to accommodate the heat loads of the specified equipment. High level sound isolation is required to ensure noise generated from this room does not invade Treatment spaces. Structural Engineer's assessment must be sought for floor load bearing capacity with respect to water treatment and pre-treatment plant equipment. Service access will be required aound the perimeter of all plant equipment. Pipework and components installed after the water inlet within this room shall not contain brass or copper.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
WTPL | Water Treatment Plant Room | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | Min Height 2400mm; Water resistant drop in tile ceiling also acceptable | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | FA | DWSC-027 | DOOR: 1600mm c/o, 1 1/2 leaf, solid core, paint | 1 | lockable | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | ELGP-106 | GPO: single, special, for equipment | 2 | pumps, as required | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | ELGP-140 | GPO: three phase, single | 1 | 3 phase, according to Manufacturer's specifications | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 4 | for use of hand tools in the room, on a separate circuit | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | FFE | FIJO-020 | BENCH: 600D, open under, laminate finish | 1 | work bench | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | FA | FLGE-003 | FLOOR FINISH: concrete, sealed, trowel | 1 |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | FA | FLSK-002 | SKIRTING: concrete, coved to 150 AFFL, sealed | 1 |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | FFE | FQBS-051 | STOOL: mobile, adj height | 1 | under bench | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | HYDR-004 | DRAIN: floor waste | 1 | floor waste must be capable of high flow rates and high temperature water (up to 95 degrees C) from the RO Water Plant | No | No | No | No | No | No | Yes | No | No
WTPL | Water Treatment Plant Room | FFE | HYGE-012 | WATER TREATMENT: reverse osmosis plant | 1 | RO Plant; details according to Manufacturer's Specifications | Yes | No | Yes | No | No | No | Yes | No | No
WTPL | Water Treatment Plant Room | FFE | HYGE-016 | PUMP: pressure booster | 2 | as needed to achieve required water pressure | Yes | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | HYGE-019 | WATER TREATMENT: brine tank | 1 |  | Yes | No | Yes | No | No | No | Yes | No | No
WTPL | Water Treatment Plant Room | SE | HYGE-020 | WATER TREATMENT: carbon filter | 2 |  | Yes | No | Yes | No | No | No | Yes | No | No
WTPL | Water Treatment Plant Room | SE | HYGE-021 | WATER TREATMENT: multimedia tank | 2 |  | Yes | No | Yes | No | No | No | Yes | No | No
WTPL | Water Treatment Plant Room | SE | HYGE-022 | WATER TREATMENT: particle filter, 1 micron | 1 |  | Yes | No | Yes | No | No | No | Yes | No | No
WTPL | Water Treatment Plant Room | SE | HYGE-023 | WATER TREATMENT: particle filter, 5 microns | 1 |  | Yes | No | Yes | No | No | No | Yes | No | No
WTPL | Water Treatment Plant Room | SE | HYGE-024 | WATER TREATMENT: softener tank | 1 |  | Yes | No | Yes | No | No | No | Yes | No | No
WTPL | Water Treatment Plant Room | SE | HYTP-008 | OUTLET: cold water | 1 | inlet for RO water treatment plant equipment | No | No | Yes | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | ITBU-002 | ALARM: equipment monitoring, water treatment malfunction | 1 | to Staff Station - Renal Unit for Plant Equipment status/ malfunction | Yes | Yes | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No