## Revision 7
HPU 500 Nuclear Medicine / PET Unit - Schedule of Accommodation, Revision 7
ENTRY / EXIT / RECEPTION / UNDOSED WAITING
AusHFG Room Code | Room / Space | SC / SC-D | 1SPECT / CT + 1 PET/CT |  | 3 SPECT / CT + 2 PET/CT |  | Remarks
|  |  | Qty | m2 | Qty | m2
WAIT-20 | Waiting | Yes | 1 | 15 | 1 | 24 | Cold' Waiting Area. Indicative area allocation based on 3 people waiting per modality including bone densitometry. Area to be confirmed based on service profile.
PLAP-10 | Play Area - Paediatric | Yes | 1 | 8 (o) | 1 | 10 (o) | Optional. Only required for services with a significant paediatric casemix.
RECL-10 | Reception / Clerical | Yes | 1 | 10 | 1 | 15 | May be shared with adjacent services in smaller units eg medical imaging.
| Office - Workstation |  |  | 4.4 | 1 | 4.4 | Administration workstations collocated with reception. Number of workstations dependent on staff profile.
INTV | Interview Room | Yes | 1 | 12 (o) | 3 | 12 (o) | Optional, depending on operational practices and local jurisdictional policies.
STPS-8 | Store - Photocopy / Stationery | Yes | 1 | 3 | 1 | 5 | Bay including multifunction device.
WCPU | Toilet - Public | Yes |  |  | 2 | 3 | 'Cold' toilets.
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 'Cold' toilets.
| Discounted Circulation |  |  | 25% |  | 25%
NUCLEAR MEDICINE - DOSED / 'HOT' WAITING
AusHFG Room Code | Room / Space | SC / SC-D | 1SPECT / CT + 1 PET/CT |  | 3 SPECT / CT + 2 PET/CT |  | Remarks
|  |  | Qty | m2 | Qty | m2
WAIT-10 | Waiting | Yes | 1 | 6 | 1 | 18 | Number of patients waiting will depend on the service profile, eg patients having cardiac scans will wait longer. 2m2 per person recommended for radiation protection purposes. A separate 'hot' play space will be required where a significant paediatric service is provided.
WCPT | Toilet – Patient | Yes | 1 | 4 | 2 | 4 | 'Hot' toilets.
BWD-1 | Bay - Water Dispenser | Yes | 1 | 1 | 1 | 1
| Discounted Circulation |  |  | 25% |  | 25%
NUCLEAR MEDICINE SCANNING & SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 1SPECT / CT + 1 PET/CT |  | 3 SPECT / CT + 2 PET/CT |  | Remarks
|  |  | Qty | m2 | Qty | m2
| Injection Room |  | 1 | 12 | 2 | 12 | For dose administration and examination. Assume 1 room shared between 2 scanners. Shielded consult room with recliner chair.
CHPT | Change Cubicle - Patient | Yes |  |  | 2 | 2 | Pre and post-scan; radiation shielded. 1 change cubicle per scanning room.
CHPT-D | Change Cubicle – Accessible | Yes | 1 | 4 | 1 | 4 | Pre and post-scan; radiation shielded.
SPECT-CT | SPECT-CT Imaging Room | Yes | 1 | 50 | 3 | 50
SPECT-CTCR | SPECT-CT Control Room | Yes | 1 | 14 | 2 | 14
| SPECT / CT Equipment / Computer Room |  | 1 | 10 (o) | 2 | 10 (o) | Optional. Includes computer mainframe / server modules for the SPECT/CT. Room temperature to be maintained for heat generating equipment. Notional space allocation only and will depend on vendor requirements.
STRT | Stress Testing Room | Yes | 1 | 20 (o) | 1 | 20 (o) | Optional depending on service profile. Trolley / bed access assumed. Similar arrangement to STRT however this needs to be a shielded room, does not require the Echo machine. The defibrillator may be located within or very near to the room.
| Bone Densitometry |  | 1 | 20 (o) | 1 | 20 (o) | Optional depending on service profile. Assumes trolley / bed access required and overhead ceiling mounted hoist.
| Nuclear Medicine Hot Lab |  | 1 | 14 | 1 | 18 | Refer to separate line item for PET hot lab. A combined hot lab, serving both Nuclear Med & PET, may be possible, however the PET hot lab must be located close to PET uptake rooms. Assumed to include Technegas and emergency eye wash. Area requirements will depend on scope of services eg dispensing of therapeutic doses, preparation of radiolabelled blood products etc.
| Nuclear Medicine Cold Lab |  | 1 | 10 (o) | 1 | 18 (o) | Optional depending on service requirements and local jurisdictional approaches. Used as a low level radioactive laboratory. Where provided the hot lab area allocation may be reduced.
| Entry Lobby - Isotope Delivery |  | 1 | 4 | 1 | 4 | Dual access from external corridor and within unit.
| Store - Phantoms |  |  | 1 |  | 2
| Radioactive Waste Holding Store |  | 1 | 5 | 1 | 8
| Discounted Circulation |  |  | 37% |  | 37%
NUCLEAR MEDICINE PATIENT HOLDING & THERAPEUTIC PROCEDURES
AusHFG Room Code | Room / Space | SC / SC-D | 1SPECT / CT + 1 PET/CT |  | 3 SPECT / CT + 2 PET/CT |  | Remarks
|  |  | Qty | m2 | Qty | m2
PBTR-H-9 | Patient Bay – Holding, 9m2 | Yes | 2 | 9 | 6 | 9 | Inpatient holding for Nuclear Medicine. Indicative number of bays noted, actual number will depend on projected volume of inpatients. Shielding requirements will depend on location.
PBTR-H-9 | Patient Bay – Holding, 9m2 | Yes |  |  | 4 | 9 (o) | Optional. For services providing therapeutic procedures. Number of bays will depend on projected activity, may include clinical trials. Shielded area. Separate treatment room/s for day procedures may be required depending on the number of spaces provided and proposed arrangement.
TRMT | Treatment Room | Yes |  |  | 1 | 14 (o) | Optional, to support therapeutic procedures depending on types of procedures provided. Shielded room.
BHWS-B | Bay - Handwashing - Type B | Yes | 1 | 1 | 2 | 1 | Additional required for therapeutic procedures.
SSTN-10 | Staff Station | Yes | 1 | 8 | 1 | 12 | For oversight of patient holding.
WCPT | Toilet – Patient | Yes | 1 | 4 | 2 | 4 | Additional required for services providing therapeutic procedures.
| Discounted Circulation |  |  | 37% |  | 37%
PET SUITE
AusHFG Room Code | Room / Space | SC / SC-D | 1SPECT / CT + 1 PET/CT |  | 3 SPECT / CT + 2 PET/CT |  | Remarks
|  |  | Qty | m2 | Qty | m2
| Uptake Room |  | 3 | 10 | 6 | 10 | Radiation shielded. Assumes ambulant patients who will be injected in a recliner. Assume 4 uptake rooms per PET/CT.
| Uptake Room - Large |  | 1 | 15 | 2 | 15 | Radiation shielded. This room will be used as an uptake room for those on beds. Number will depend on service profile, increased number required for paediatric services. Children will often be induced in the Uptake room so access to anaesthetic gases is required.
CHPT-D | Change Cubicle – Accessible | Yes | 1 | 4 | 2 | 4 | Pre and post-scan; radiation shielded
WCPT | Toilet – Patient | Yes | 1 | 4 | 1 | 4 | Hot' toilets - Radiation shielded.
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | Consider automated door given heavy weight due to shielding is difficult for disabled patients to manage.
PET-CT | PET-CT Imaging Room | Yes | 1 | 50 | 2 | 50 | This will also accommodate Total Body PET systems, however consideration needs to be given to shielding requirements and the number of uptake rooms given the faster throughput.
| PET-CT Control Room | Yes | 1 | 14 | 2 | 14 | Includes communication (intercom) connection to PET/CT and Uptake rooms.
| PET/ CT Computer / Equipment Room |  | 1 | 10 (o) | 2 | 10 (o) | Optional. Includes computer mainframe / server modules for the PET/CT. Room temperature to be maintained for heat generating equipment. Notional space allocation only and will depend on vendor requirements.
| PET/CT - Alcove for Automated Infusion System |  | 2 | 2 (o) | 3 | 2 (o) | Optional. Shared between 2 uptake rooms for location of automated infusion system where provided via a port.
BHWS-B | Bay - Handwashing – Type B | Yes | 1 | 1 | 2 | 1 | In corridor, 1 per 4 uptake rooms.
| PET Hot Laboratory |  | 1 | 14 | 1 | 18 | Will be adjacent to uptake rooms. Includes emergency eye wash.
| Radiopharmaceutical Laboratory |  | 1 | 40 (o) | 1 | 40 (o) | Optional, specialised services only where manufacturing is undertaken. Indicative minimum area allocation for a radiopharmaceutical lab noted. Actual area to be determined based on the scale and scope of manufacturing and associated activities across nuclear medicine and PET services.
BES | Bay – Emergency Shower | Yes | 1 | 2 | 1 | 2 | Radiation shielded. Locate outside radiopharmaceutical lab where provided.
| Discharge Lounge |  | 1 | 8 | 1 | 12 | Radiation shielded. Collocate with Beverage Bay. Operational policy relating to patients on trollies requiring transfer to be confirmed.
| Discounted Circulation |  |  | 37% |  | 37%
SHARED SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 1SPECT / CT + 1 PET/CT |  | 3 SPECT / CT + 2 PET/CT |  | Remarks
|  |  | Qty | m2 | Qty | m2
CLN-10 | Clean Store | Yes | 1 | 10 | 1 | 14 | Clean consumables.
STEQ-14 | Store - Equipment | Yes | 1 | 12 | 1 | 20
BLIN | Bay – Linen | Yes | 1 | 2 | 2 | 2 | For inpatient holding & uptake rooms
BMEQ | Bay - Mobile Equipment | Yes | 1 | 2 | 1 | 3 | Mobile equipment requirements to be confirmed.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | Requires careful consideration of location. Rapid access from the Stress Test Room, if defib not located within the room, and other patient care areas is required.
BWP | Bay - Wheelchair Park | Yes | 1 | 2 | 1 | 4
BBEV-OP | Bay - Beverage, Open Plan | Yes | 1 | 4 | 1 | 4
CLRM-5 | Cleaner's Room | Yes | 1 | 5 | 1 | 5 | Dedicated to unit to avoid radioactive contamination.
DTUR-8 | Dirty Utility | Yes | 1 | 8 | 1 | 10 | Refer to Section 2.2.14 re radioactive waste disposal.
DISP-8 | Disposal Room | Yes |  |  | 1 | 8 | Note separate radioactive waste store included above. Assume shared with adjacent department for smaller service.
| Discounted Circulation |  |  | 37% |  | 37%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 1SPECT / CT + 1 PET/CT |  | 3 SPECT / CT + 2 PET/CT |  | Remarks
|  |  | Qty | m2 | Qty | m2
REPR | Reporting Room |  | 1 | 18 | 1 | 36 | Assume 1-2 workstations per scanner with 6m2 per reporting workstation.
OFF-S9 | Office- Single Person | Yes |  | 9 |  | 9 | Number and area allocation will depend on staff profile and local jurisdictional policies.
| Office - Workstation |  |  | 4.5 |  | 4.5 | Number and area allocation will depend on staff profile and local jurisdictional policies.
INTV | Interview Room | Yes |  | 9 |  | 9 | Number dependent on service requirements.
MEET-L-20 | Meeting Room | Yes | 1 | 15 | 1 | 25 | Size will depend on number of people to be accomodated and local jurisdictional policies.
SRM-15 | Staff Room | Yes | 1 | 16 | 1 | 24 | Area will depend on staffing profile and operational policies.
BPROP | Bay - Property, Staff | Yes | 1 | 2 | 1 | 3
WCST | Toilet – Staff | Yes | 2 | 3 | 4 | 3 | Number dependent on service profile.
SHST | Shower – Staff | Yes | 1 | 3 (o) | 1 | 3 (o) | Optional depending on approach to end of trip facilities.
| Discounted Circulation |  |  | 25% |  | 25%