## Revision 7 Specimen Collection
HPU 550 Pathology - Schedule of Accommodation, Revision 7
Outpatient Specimen Collection
SPECIMEN COLLECTION
AusHFG Room Code | Room / Space | SC / SC-D | Qty | m2 | Remarks
WAIT-10 | Waiting | Yes | 1 | 8
RECL-10 | Reception / Clerical | Yes | 1 | 10 (o) | Optional. May be shared with adjacent service.
BMFD-3 | Bay - Multifunction Device | Yes | 1 | 3 (o) | Optional. May be shared with adjacent service.
SPECC | Specimen Collection Bay | Yes | 2 | 9
BHWS-B | Bay - Handwashing, Type B | Yes | 1 | 1
| Specimen Collection Room |  | 1 | 12 (o) | Optional, depending on service requirements. Assumes an enclosed room with basin. May require dual egress depending on jurisdictional policies and risk assessment. Paediatric services will require access to bed and chair (or combined treatment recliner) and fit out / technology to support patient distraction. Includes handwash basin.
WCPT | Toilet - Patient | Yes | 1 | 4 | Specimen collection. 6m2 if accessible access required. May have pass-through hatch.
CLN-10 | Clean Store | Yes | 1 | 9 | For storage of consumables. Includes underbench fridge for glucose tolerance drinks.
BMEQ-4 | Bay - Mobile Equipment | Yes | 1 | 4 | Phlebotomy trolleys. May be combined with clean store to support workflow of stocking trolleys with consumables.
BPTS | Bay - Pneumatic Tube | Yes | 1 | 1 (o) | Optional, depending on location and hospital- wide approach. Bench space for packing may be required depending on workflows.
BPATH | Bay - Pathology | Yes | 1 | 3 (o) | Optional, depending on scope of services provided.
BLIN | Bay - Linen | Yes | 1 | 1 (o) | Optional, depending on opportunity to share with adjacent department or use of disposable linen.
CLUP-7 | Clean -Up Room | Yes | 1 | 7 (o) | Optional, depending on opportunity to share with adjacent department. Includes area to wash and dry tourniquets and dirty linen skip.
| Discounted Circulation |  | 32%

## Revision 7 Pathology
HPU 550 Pathology - Schedule of Accommodation, Revision 7
Pathology Unit
RECEPTION / PRE-ANALYTICAL ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2
RECL-12 | Reception - Visitor and Specimen | Yes | 1 | 12 | 1 | 12 | 1 | 20 | Includes specimens delivered via staff, couriers and pneumatic tube.
| Pre-Analytical Zone |  |  |  | 1 | 20 | 1 | 35 | Area must be continuous with the Core Laboratory to support optimal specimen workflows.
| Discounted Circulation |  | 32% |  | 32% |  | 32%
LABORATORIES
AusHFG Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2
| Laboratory - Core |  | 1 | 50 | 1 | 90 | 1 | 240 | At a minimum the core lab will include transfusion services, haematology and chemical pathology. Area allocations noted are indicative and will depend on the role of the unit within the network, volume of activity and analyser capacity. For Scenario 3 the recommended area is based on a major regional referral hospital of approximately 450 beds. Actual area requirements will depend on local service requirements. Includes area for new equipment commissioning, handwash basins, emergency shower/eye wash, fridges, freezers and other storage. Area requirement is subject to test fit of lab benches to achieve AS/NZS 2982:2010 (1400 clearance between facing benches).
| Laboratory - Microbiology |  |  |  | 1 | 30 (o) |  | 100 | Optional if the service cannot be provided in a timely manner by a higher level networked service. Areas are indicative only, actual requirements will depend on the volume of activity.
| Laboratory - Anatomical Pathology |  |  |  | 1 | 30 (o) |  | 200 | Optional if the service cannot be provided in a timely manner by a higher level networked service. Areas are indicative only, actual requirements will depend on the volume of activity.
| Discounted Circulation |  | 32% |  | 32% |  | 32%
SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2
| Store - Cool Room / Refrigerators/ Freezers |  | 1 | 6 | 1 | 12 | 1 | 20 | Specimens and reagants.
CLN-10 | Clean Store | Yes | 1 | 6 | 1 | 12 | 1 | 30 | Consumables store. May require additional capacity to store clinical trolleys depending on operational arrangements. May be combined with general store for efficient use of storage.
STGN | Store - General | Yes |  |  | 1 | 14 | 1 | 20 | May be combined with clean store for efficient use of storage. Floor loading will need to be considered if a compactus is being provided.
| Store - Flammable Liquids |  | 1 | 2 | 1 | 3 | 1 | 5
CLUP-7 | Clean-Up Room |  |  |  | 1 | 7 | 1 | 10 | Clean up functions included in core laboratory area allocation for small unit.
CLRM-5 | Cleaner's Room | Yes |  |  | 1 | 5 | 1 | 5 | May be shared with collocated departments for small and medium sized units.
DISP-8 | Disposal Room | Yes |  |  | 1 | 8 | 1 | 8 | Assume disposal room is shared with adjacent department for smaller unit. May be shared with collocated departments for medium sized units.
AHBBF | After-Hours Blood Fridge |  | 1 | 8 | 1 | 10 |  |  | Collocate with the blood bank.Secure but accessible after hours for emergencies. Not included in large hospital unit given 24/7 pathology access.
| Discounted Circulation |  | 32% |  | 32% |  | 32%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2
OFF-S9 | Office - Single Person, 9m2 | Yes | 1 | 9 |  | 9 |  | 9 | The number of staff work areas will depend on local requirements based on the staff profile and local jurisdictional policies. Pathology reporting will require quiet work areas. Larger sized offices may be required to support teaching and training requirements and accomodation of microscopes, depending on local policies. Include vision panel for oversight of labs.
| Office - Workstation, 5.5m2 |  |  |  |  | 5.5 |  | 5.5 | The number of workstations will depend on local requirements based on the staff profile and local jurisdictional policies.
BMFD-3 | Bay - Multifunction Device | Yes |  |  | 1 | 3 |  | 3
MEET-L-15 | Meeting Room, 15m2 | Yes |  |  | 1 | 15 | 1 | 15 | Meeting room size is indicative and will depend on local requirements.
MEET-L-30 | Meeting Room, 30m2 | [5 empty] | 1 | 30 | Meeting room size is indicative and will depend on local requirements.
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | 1 | 3 |  |  |  |  | Supports 24/7 access for staff. Requires oversight of the laboratory. Must be external to PC2 facility where provided.
SRM-15 | Staff Room |  |  |  | 1 | 12 | 1 | 20 | Supports 24/7 access for staff. Indicative area noted, requirements will depend on the staff profile. Requires oversight of the core laboratory. Must be external to PC2 facility where provided.
BPROP | Bay - Property, Staff | Yes |  |  | 1 | 1 | 1 | 3 | Smaller units will require shared access to staff amenities.
SHST | Shower - Staff, 3m2 | Yes |  |  | 1 | 3 (o) | 1 | 3 | Optional.
WCST | Toilet - Staff, 3m2 | Yes |  |  | 2 | 3 | 4 | 3 | Indicative, number will depend on staff profile. Smaller units will required shared access to staff amenities.
| Discounted Circulation |  | 25% |  | 25% |  | 25%