## 2 Bunkers
2 Bunkers
AusHFG Room Code | Room / Space | SC / SC-D | Qty | m2 | Remarks
ENTRY / RECEPTION / WAITING
AIRLE-10 | Airlock - Entry, 10m2 | Yes | 1 | 10 | Assumes 2 sets of double automatic doors double 900mm leaf. Not required if entry is provided through an internal entry.
WAIT-20 | Waiting, 20m2 | Yes | 1 | 20 | In 2 bunker scenario, waiting space is shared with clinics.
RECL-10 | Reception / Clerical, 10m2 | Yes | 1 | 20 | 2 staff.
OFF-2P | Office - 2 Person Shared, 12m2 | Yes | 1 | 12 | 2 and 3 staff.
STPS-8 | Store - Photocopy / Stationery, 8m2 | Yes | 1 | 8
BWC | Bay - Wheelchair | Yes | 1 | 4 | Trolleys and wheelchairs.
WCPU-3 | Toilet - Public, 3m2 | Yes | 2 | 3
WCAC | Toilet - Accessible, 6m2 | Yes | 1 | 6
BPH | Bay - Public Telephone | Yes | 1 | 1 | Taxi phones.
BVM-3 | Bay - Vending Machines | Yes | 1 | 3(o) | Optional, depending on local approaches and service location.
| Resource Room |  | 1 | 12 | Education and/or information.
| Volunteers' Workroom |  | 1 | 12 | Optional.
| Discounted Circulation |  | 30%
OUTPATIENT CLINICS
CONS | Consult Room | Yes | 4 | 12
CONS | Consult Room | Yes | 2 | 14 | Sized to accommodate up to 3 staff.
PROC-16 | Procedure Room, 16m2 | Yes | 1 | 16
INTF | Interview Room | Yes | 1 | 12
OFF-CLW | Office – Clinical Workroom | Yes | 1 | 12 | A coordination / staff write-up space. Also used for clinical review.
WCPT | Toilet - Patient, 4m2 | Yes | shared with reception
WAIT-30 | Waiting, 30m2 | Yes | shared with reception
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | 1 | 3
| Discounted Circulation |  | 30%
PATIENT AREAS – PLANNING AND TREATMENT
WAIT-S | Waiting - Sub, 5m2 | Yes | 1 | 5
| Toilet / Change - Patient |  | 1 | 5
| Planning CT / Simulator |  | 1 | 45 | Simulation and planning.
CTCR | CT Scanning, Control Room | Yes | 1 | 14
| Image Review Room |  | - | -
| Bay - Patient Trolley |  | 1 | 4
BS-1 | Bay - Storage | Yes | 1 | 2 | Space to store a blanket warmer and ice machine.
BRES | Bay - Resuscitation | Yes | 1 | 1.5
STEQ-14 | Store - Equipment | Yes | 1 | 9
OFF-S9 | Office, Single Person, 9m2 | Yes | - | - | RT Head of Planning.
| Discounted Circulation |  | 30%
MOULD ROOM / APPLIANCE FABRICATION
| Fitting Room |  |  |  | In 2 room units, CT simulation room can be used.
| Moulding Room - Clean |  | 1 | 15
| Workroom - Dirty |  | 1 | 9 | Noisy machinery used.
STEQ-14 | Store - Equipment | Yes | 1 | 6
| Discounted Circulation |  | 30%
PLANNING AREAS
OFF-S9 | Office - Single Person, 9m2 | Yes |  | 9 | To be allocated to Manager Planning and Manager Planning Treatment.
OFF-2P | Office - 2 Person Shared, 12m2 | Yes |  | 12 | For booking clerks.
| Planning Room |  | 1 | 50
| Discounted Circulation |  | 35%
TREATMENT BUNKERS
WAIT-10 | Waiting, 10m2 | Yes | 1 | 7 | Family etc.
CHPT | Change Cubicle - Patient, 2m2 | Yes | 2 | 2
CHPT-D | Change Cubicle - Accessible, 4m2 | Yes | 1 | 4
WCPT | Toilet - Patient, 4m2 | Yes | 1 | 4
INTF | Interview Room | Yes | 1 | 9 | May also provide private waiting.
WAIT-S | Waiting - Sub, 5m2 | Yes | 2 | 3 | Located outside each bunker for those changed into gowns.
| Linear Accelerator |  | 2 | 150 | See first note above re. 150m2 spatial allocation.
| Control Room – Linear Accelerator |  | 2 | 22
| Orthovoltage Room |  |  | - | Includes HT generator within room. Inclusion may depend on range of cases treated.
| Control Room - Orthovoltage |  |  | -
BLIN | Bay - Linen | Yes | 1 | 2
BHWS-B | Bay – Handwashing, Type B | Yes | 1 | 1
STEQ-14 | Store - Equipment | Yes | 1 | 9 | Includes space for patient specific immobilisation equipment.
| Discounted Circulation |  | 35%
TREATMENT - BRACHYTHERAPY SUITE
| Brachytherapy Bunker |  |  | - | Assumes permanent seed implantation.
| Control Room |  |  | -
SCRB-6 | Scrub-Up / Gowning, 6m2 | Yes |  | - | 2 sinks.
PBTR-H-9 | Patient Bay - Holding / Recovery | Yes |  | -
| Seed Store and Loading |  |  | -
STGN-9 | Store - General, 9m2 | Yes |  | - | Sterile consumables associated with procedures.
| Toilet / Change - Patient |  |  | -
Discounted Circulation
PATIENT HOLDING AND RECOVERY
SSTN-10 | Staff Station | Yes | 1 | 12 | Open plan with Treatment Bays.
PBTR-H-9 | Patient Bay - Holding, 9m2 | Yes | 2 | 9 | Open plan with Staff Station.
1BR-H-12 | 1 Bedroom – Holding, 12m2 |  | - | - | May accommodate a bed or recliner chair and provide isolation if required.
BHWS-B | Bay - Handwashing, Type B | Yes | 1 | 1
ENS-ST | Ensuite - Standard, 5m2 | Yes | - | -
WCPT | Toilet - Patient, 4m2 | Yes | 1 | 4
BLIN | Bay - Linen | Yes | 1 | 2 | Part of open plan area.
BRES | Bay Resuscitation | Yes | 1 | 1.5 | Part of open plan area.
OFF-S9 | Office – Single Person, 9m2 | Yes | 1 | 9 | For nursing manager.
CLUR-12 | Clean Utility / Medication Room | Yes | 1 | 12 | Accessible to other areas of the Unit.
DTUR-10 | Dirty Utility, 10m2 | Yes | 1 | 10 | Accessible to other areas of the Unit.
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | - | -
| Discounted Circulation |  | 30%
CLINICAL SUPPORT AREAS
| Physics Laboratory |  | 1 | 25
| Physics Store |  | 1 | 15 | Locate close to bunkers so access to water tank is facilitated.
| Workshop - Electrical |  | 1 | 30 | Includes write-up space for technicians / visiting contractors and storage for spare parts.
| Workshop - Mechanical |  | 1 | 5.5 | Noise generated in this room.
CLRM-5 | Cleaner's Room, 5m2 | Yes | 1 | 5
DISP-8 | Disposal Room, 8m2 | Yes | 1 | 8 | If combined with Dirty Utility, 1 x 14m2.
| Discounted Circulation |  | 30%
STAFF OFFICES AND AMENITIES
OFF-S12 | Office - Single Person, 12m2 | Yes | 1 | 12 | Clinical Director.
OFF-S9 | Office - Single Person, 9m2 | Yes |  | 9 | To be allocated to staff specialists and department heads (e.g. Radiation Therapy, Medical Physics etc). Numbers will be dependent on organisational structure and staff establishment.
| Office - Workstation, 5.5m2 |  |  | 5.5 | To be allocated to staff including clerical, data managers, IT staff, educators, clinical nurse consultants, medical physicists, registrars and researchers etc. Number will be dependent on staff establishment.
| Office - Workstation, 4.4m2 |  | 2 | 4.4 | Hot desks for visiting staff and students.
MEET-L-30 | Meeting Room, 30m2 | Yes | 1 | 30
MEET-L-20 | Meeting Room, 20m2 | Yes | - | -
MEET-9 | Meeting Room, 9m2 | Yes | 1 | 1 x 9
STPS-8 | Store – Photocopier / Stationery, 8m2 | Yes | Shared
SRM | Staff Room | Yes | 1 | 20
PROP-2 | Property Bay – Staff | Yes | 1 | 3
WCST | Toilet - Staff, 3m2 | Yes | 3 | 3 | To be distributed throughout the Unit.
SHST | Shower - Staff, 3m2 | Yes | 1 | 3
| Discounted Circulation |  | 25%

## 4 Bunkers
4 Bunkers
AusHFG Room Code | Room / Space | SC / SC-D | Qty | m2 | Remarks
ENTRY / RECEPTION / WAITING
AIRLE-10 | Airlock - Entry, 10m2 | Yes | 1 | 10 | Assumes 2 sets of double automatic doors double 900mm leaf. Not required if entry is provided through an internal entry.
WAIT-20 | Waiting, 20m2 | Yes | 1 | 20 | In 2 bunker scenario, waiting space is shared with clinics.
RECL-10 | Reception / Clerical, 10m2 | Yes | 1 | 20 | 2 staff.
OFF-2P | Office - 2 Person Shared, 12m2 | Yes | 1 | 15 | 2 and 3 staff.
STPS-8 | Store - Photocopy / Stationery, 8m2 | Yes | 1 | 8
BWC | Bay - Wheelchair | Yes | 1 | 6 | Trolleys and wheelchairs.
WCPU-3 | Toilet - Public, 3m2 | Yes | 2 | 3
WCAC | Toilet - Accessible, 6m2 | Yes | 1 | 6
BPH | Bay - Public Telephone | Yes | 1 | 1 | Taxi phones.
BVM-3 | Bay - Vending Machines | Yes | 1 | 3(o) | Optional, depending on local approaches and service location.
| Resource Room |  | 1 | 15 | Education and/or information.
| Volunteers' Workroom |  | 1 | 12 | Optional.
| Discounted Circulation |  | 30%
OUTPATIENT CLINICS
CONS | Consult Room | Yes | 7 | 12
CONS | Consult Room | Yes | 3 | 14 | Sized to accommodate up to 3 staff.
PROC-16 | Procedure Room, 16m2 | Yes | 1 | 16
INTF | Interview Room | Yes | 1 | 12
OFF-CLW | Office – Clinical Workroom | Yes | 1 | 15 | A coordination / staff write-up space. Also used for clinical review.
WCPT | Toilet - Patient, 4m2 | Yes | 1 | 4
WAIT-30 | Waiting, 30m2 | Yes | 1 | 30
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | 1 | 3
| Discounted Circulation |  | 30%
PATIENT AREAS – PLANNING AND TREATMENT
WAIT-S | Waiting - Sub, 5m2 | Yes | 1 | 10
| Toilet / Change - Patient |  | 1 | 5
| Planning CT / Simulator |  | 2 | 45 | Simulation and planning.
CTCR | CT Scanning, Control Room | Yes | 2 | 14
| Image Review Room |  | 1 | 10
| Bay - Patient Trolley |  | 1 | 6
BS-1 | Bay - Storage | Yes | 1 | 2 | Space to store a blanket warmer and ice machine.
BRES | Bay - Resuscitation | Yes | 1 | 1.5
STEQ-14 | Store - Equipment | Yes | 1 | 12
OFF-S9 | Office, Single Person, 9m2 | Yes | 1 | 9 | RT Head of Planning.
| Discounted Circulation |  | 30%
MOULD ROOM / APPLIANCE FABRICATION
| Fitting Room |  |  |  | In 2 room units, CT simulation room can be used.
| Moulding Room - Clean |  | 1 | 15
| Workroom - Dirty |  | 1 | 9 | Noisy machinery used.
STEQ-14 | Store - Equipment | Yes | 1 | 6
| Discounted Circulation |  | 30%
PLANNING AREAS
OFF-S9 | Office - Single Person, 9m2 | Yes |  | 9 | To be allocated to Manager Planning and Manager Planning Treatment.
OFF-2P | Office - 2 Person Shared, 12m2 | Yes |  | 12 | For booking clerks.
| Planning Room |  | 1 | 90
| Discounted Circulation |  | 35%
TREATMENT BUNKERS
WAIT-10 | Waiting, 10m2 | Yes | 1 | 12 | Family etc.
CHPT | Change Cubicle - Patient, 2m2 | Yes | 4 | 2
CHPT-D | Change Cubicle - Accessible, 4m2 | Yes | 2 | 4
WCPT | Toilet - Patient, 4m2 | Yes | 2 | 4
INTF | Interview Room | Yes | 2 | 9 | May also provide private waiting.
WAIT-S | Waiting - Sub, 5m2 | Yes | 4 | 3 | Located outside each bunker for those changed into gowns.
| Linear Accelerator |  | 4 | 150 | See first note above re. 150m2 spatial allocation.
| Control Room – Linear Accelerator |  | 4 | 22
| Orthovoltage Room |  | 1 | 45(o) | Includes HT generator within room. Inclusion may depend on range of cases treated.
| Control Room - Orthovoltage |  | 1 | 12(o)
BLIN | Bay - Linen | Yes | 1 | 2
BHWS-B | Bay – Handwashing, Type B | Yes | 1 | 1
STEQ-14 | Store - Equipment | Yes | 2 | 9 | Includes space for patient specific immobilisation equipment.
| Discounted Circulation |  | 35%
TREATMENT - BRACHYTHERAPY SUITE
| Brachytherapy Bunker |  | 1 | 130 | Assumes permanent seed implantation.
| Control Room |  | 1 | 15
SCRB-6 | Scrub-Up / Gowning, 6m2 | Yes | 1 | 6 | 2 sinks.
PBTR-H-9 | Patient Bay - Holding / Recovery | Yes | 1 | 9
| Seed Store and Loading |  | 1 | 9
STGN-9 | Store - General, 9m2 | Yes | 1 | 9 | Sterile consumables associated with procedures.
| Toilet / Change - Patient |  | 1 | 5
| Discounted Circulation |  | 35%
PATIENT HOLDING AND RECOVERY
SSTN-10 | Staff Station | Yes | 1 | 12 | Open plan with Treatment Bays.
PBTR-H-9 | Patient Bay - Holding, 9m2 | Yes | 3 | 9 | Open plan with Staff Station.
1BR-H-12 | 1 Bedroom – Holding, 12m2 |  | 1 | 12 | May accommodate a bed or recliner chair and provide isolation if required.
BHWS-B | Bay - Handwashing, Type B | Yes | 1 | 1
ENS-ST | Ensuite - Standard, 5m2 | Yes | 1 | 5
WCPT | Toilet - Patient, 4m2 | Yes | 1 | 4
BLIN | Bay - Linen | Yes | 1 | 2 | Part of open plan area.
BRES | Bay Resuscitation | Yes | 1 | 1.5 | Part of open plan area.
OFF-S9 | Office – Single Person, 9m2 | Yes | 1 | 9 | For nursing manager.
CLUR-12 | Clean Utility / Medication Room | Yes | 1 | 14 | Accessible to other areas of the Unit.
DTUR-10 | Dirty Utility, 10m2 | Yes | 1 | 10 | Accessible to other areas of the Unit.
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | 1 | 4
| Discounted Circulation |  | 30%
CLINICAL SUPPORT AREAS
| Physics Laboratory |  | 1 | 40
| Physics Store |  | 2 | 15 | Locate close to bunkers so access to water tank is facilitated.
| Workshop - Electrical |  | 1 | 45 | Includes write-up space for technicians / visiting contractors and storage for spare parts.
| Workshop - Mechanical |  | 1 | 5.5 | Noise generated in this room.
CLRM-5 | Cleaner's Room, 5m2 | Yes | 1 | 5
DISP-8 | Disposal Room, 8m2 | Yes | 1 | 8 | If combined with Dirty Utility, 1 x 14m2.
| Discounted Circulation |  | 30%
STAFF OFFICES AND AMENITIES
OFF-S12 | Office - Single Person, 12m2 | Yes | 1 | 12 | Clinical Director.
OFF-S9 | Office - Single Person, 9m2 | Yes |  | 9 | To be allocated to staff specialists and department heads (e.g. Radiation Therapy, Medical Physics etc). Numbers will be dependent on organisational structure and staff establishment.
| Office - Workstation, 5.5m2 |  |  | 5.5 | To be allocated to staff including clerical, data managers, IT staff, educators, clinical nurse consultants, medical physicists, registrars and researchers etc. Number will be dependent on staff establishment.
| Office - Workstation, 4.4m2 |  | 4 | 4.4 | Hot desks for visiting staff and students.
MEET-L-30 | Meeting Room, 30m2 | Yes | 1 | 30
MEET-L-20 | Meeting Room, 20m2 | Yes | 1 | 20
MEET-9 | Meeting Room, 9m2 | Yes | 1 | 9
STPS-8 | Store – Photocopier / Stationery, 8m2 | Yes | 1 | 8
SRM | Staff Room | Yes | 1 | 35
PROP-2 | Property Bay – Staff | Yes | 1 | 6
WCST | Toilet - Staff, 3m2 | Yes | 5 | 3 | To be distributed throughout the Unit.
SHST | Shower - Staff, 3m2 | Yes | 1 | 3
| Discounted Circulation |  | 25%